## parameters
| version | converged | name | f_hz | sn_mva | OPF_converged
0 | 2.9.0 | TRUE | WACS | 50 | 1 | FALSE

## bus
| name | vn_kv | type | zone | in_service
25 | ЭГРЭС-1 | 500 | b | 2 | TRUE
26 | ЭК-1150 | 500 | b | 2 | TRUE
28 | ЭГРЕС-2 500 | 500 | b | 2 | TRUE
30 | еэк-20-бл5-8 | 20 | b | 2 | TRUE
31 | ЕЭК | 500 | b | 2 | TRUE
33 | ПС-ЕЭК 220 | 220 | b | 2 | TRUE
39 | ЭГРЭС-1 220 | 220 | b | 2 | TRUE
50 | эгрэс-1 бл3-2 | 20 | b | 2 | TRUE
51 | эгрэс-1 20 | 20 | b | 2 | TRUE
60 | эгрэс-2 20 | 20 | b | 2 | TRUE
63 | Ташкент | 500 | b | 18 | FALSE
129 | ЦГПП | 500 | b | 5 | TRUE
130 | ПС-ЦГПП 220 | 220 | b | 5 | TRUE
147 | АВРОРА 500 | 500 | b | 7 | TRUE
175 | Кокшетау | 500 | b | 6 | TRUE
180 | ПС-ЕГПП | 500 | b | 5 | TRUE
224 | Таш.ГРЭС | 500 | b | 18 | TRUE
240 | Усть-Каменогорск | 500 | b | 1 | TRUE
241 | У-К | 220 | b | 1 | TRUE
306 | Оскаровка 220 | 220 | b | 3 | TRUE
310 | Нура 220 | 220 | b | 3 | TRUE
325 | Нура | 500 | b | 3 | TRUE
355 | Кар.ГРЭС-2 | 220 | b | 3 | TRUE
356 | Кар.ГРЭС-2 110 | 110 | b | 3 | TRUE
455 | Кумколь 110 | 110 | b | 4 | TRUE
465 | Каражал 220 | 220 | b | 4 | TRUE
466 | Жезказган 220 | 220 | b | 4 | TRUE
467 | Кумколь 220 | 220 | b | 4 | TRUE
468 | Агадырь 220 | 220 | b | 4 | TRUE
469 | Агадырь | 500 | b | 4 | TRUE
472 | Балхашская 110 | 110 | b | 4 | TRUE
473 | Балхашская | 220 | b | 4 | TRUE
475 | Мойынты | 220 | b | 4 | TRUE
480 | ЖЕЗКАЗГАН | 500 | b | 4 | TRUE
576 | Сокол | 500 | b | 8 | TRUE
577 | Житикара | 500 | b | 8 | TRUE
590 | Костанай | 500 | b | 8 | TRUE
800 | Жамбыл | 500 | b | 11 | TRUE
801 | Жамбыл 220 | 220 | b | 11 | TRUE
805 | жгрэс-220 | 220 | b | 11 | TRUE
814 | Аспара | 220 | b | 9 | TRUE
830 | Шымкент | 500 | b | 12 | TRUE
831 | Шымкент 220 | 220 | b | 12 | TRUE
839 | Жылга | 220 | b | 12 | TRUE
840 | Кентау | 220 | b | 12 | TRUE
842 | Миргалимсай | 220 | b | 12 | TRUE
843 | Шымкентская | 220 | b | 12 | TRUE
862 | Кызылорда 220 | 220 | b | 13 | TRUE
865 | Жанакорган | 220 | b | 13 | TRUE
869 | Ру-6 | 220 | b | 13 | TRUE
900 | ЮКГРЭС | 500 | b | 9 | TRUE
901 | ЮкГрэс 220 | 220 | b | 9 | TRUE
902 | Алматы | 500 | b | 9 | TRUE
903 | Алматы 220 | 220 | b | 9 | TRUE
904 | АТЭЦ-3 | 220 | b | 9 | TRUE
905 | АТЭЦ-3 110 | 110 | b | 9 | TRUE
907 | Робот | 220 | b | 9 | TRUE
911 | Чилик | 220 | b | 9 | TRUE
912 | ПС-7 АХБК | 220 | b | 9 | TRUE
913 | ПС-7 АХБК 110 | 110 | b | 9 | TRUE
918 | Западная 220 | 220 | b | 9 | TRUE
928 | Медео | 220 | b | 9 | TRUE
932 | Шу 220 | 220 | b | 9 | TRUE
935 | Мойнакская ГЭС | 220 | b | 9 | TRUE
938 | Алма | 500 | b | 9 | TRUE
939 | Алма 220 | 220 | b | 9 | TRUE
953 | Коян-Кос | 220 | b | 9 | TRUE
980 | Семей | 500 | b | 19 | TRUE
981 | Семей 220 | 220 | b | 19 | TRUE
986 | Актогай | 500 | b | 1 | TRUE
987 | Талдыкорган | 500 | b | 10 | TRUE
988 | Талдыкорган 220 | 220 | b | 10 | TRUE
1621 | Рубцовск | 500 | b | 15 | TRUE
1630 | Барнаул | 500 | b | 15 | TRUE
1631 | Заря | 500 | b | 15 | TRUE
1636 | Генерация Сибири | 500 | b | 15 | TRUE
1660 | Алтай | 500 | b | 15 | TRUE
1817 | ТАВРИЧЕСКАЯ | 500 | b | 17 | TRUE
1850 | ИРТЫШСКАЯ | 500 | b | 17 | TRUE
1852 | Витязь | 500 | b | 17 | TRUE
1853 | Восход | 500 | b | 17 | TRUE
1916 | Главная 220 | 220 | b | 50 | TRUE
2918 | Фрунзе 220 | 220 | b | 50 | TRUE
2919 | Фрунзе | 500 | b | 50 | TRUE
2921 | ГЕНЕРАЦИЯ ЦА-1 | 500 | b | 51 | TRUE
2925 | ТашкентТэс 220 | 220 | b | 18 | TRUE
2952 | Кемин 220 | 220 | b | 51 | TRUE
4703 | Козырево | 500 | b | 16 | TRUE
4705 | Челябинск | 500 | b | 0 | TRUE
4727 | Курган | 500 | b | 16 | TRUE
4782 | Шагол | 500 | b | 16 | TRUE
4785 | Магнитагорская | 500 | b | 16 | TRUE
4790 | Ириклинская ГРЭС | 500 | b | 16 | TRUE
4799 | Троицская ГРЭС | 500 | b | 16 | TRUE
7201 | пр/уз. Семей У-К | 220 | b | 1 | TRUE
7202 | пр/уз. ЕЭК Семей | 220 | b | 20 | TRUE
7203 | пр/уз. Эгрэс-1 ЕЭК | 220 | b | 2 | TRUE
7204 | пр/уз.ЦГПП-ЭГРЭС-1 | 220 | b | 2 | TRUE
7205 | пр/уз.ЦГПП-Осакоровка | 220 | b | 5 | TRUE
7206 | пр/уз.ЭГРЭС 1 Осакоровка | 220 | b | 3 | TRUE
7208 | пр/уз.КарГРЭС-Нура | 220 | b | 3 | TRUE
7209 | пр/уз.Каргрэс-Каражал | 220 | b | 3 | TRUE
7210 | пр/уз.Каргрэс-Агадырь | 220 | b | 3 | TRUE
7211 | пр/уз.Каргрэс - Балхашская | 220 | b | 3 | TRUE
7212 | пр/уз ЮкГРЭС ШУ | 220 | b | 9 | TRUE
7213 | пр/уз Алматы Алма | 220 | b | 9 | TRUE
7214 | пр/уз Главная Кемин | 220 | b | 50 | TRUE
7215 | пр/уз Фрунзе Кемин | 220 | b | 51 | TRUE
7216 | пр/уз Жамбыл Шымкент | 220 | b | 12 | TRUE
7217 | пр/уз ГлавнаяФрунзе | 220 | b | 50 | TRUE
7218 | пр/уз ТалдыкорганРобот | 220 | b | 9 | TRUE
7219 | пр/уз МойынтыЮкгрэс | 220 | b | 9 | TRUE
7221 | пр/уз ЖезказганКаражал | 220 | b | 4 | TRUE
7223 | пр/уз жгрэс- Фрунзе | 220 | b | 11 | TRUE
7224 | пр/уз Кентау Жамбыл 220 | 220 | b | 12 | TRUE
7225 | Пр/уз Шымкент-220/Жылга | 220 | b | 12 | TRUE
7226 | пр/уз Ру-6/Кызылорда | 220 | b | 13 | TRUE
7227 | пр/уз Кызылорда-Кумколь | 220 | b | 14 | TRUE
7228 | ГНПС | 220 | b | 14 | TRUE
7229 | пр/уз Кар.ГРЭС-2 - Осакоровка | 220 | b | 3 | TRUE
9917 | Барабинская | 500 | b | 15 | TRUE
9932 | ЧУ | 500 | b | 9 | TRUE
10000 | ЮжУГРЭС | 500 | b | 16 | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
30 | еэк-20-бл5-8 | 30 | 12 | 3 | 0 | 0 |  | 1 | TRUE | wye
31 | ЕЭК | 31 | 430 | 120 | 0 | 0 |  | 1 | TRUE | wye
33 | ПС-ЕЭК 220 | 33 | 522.8 | 302 | 0 | 0 |  | 1 | TRUE | wye
39 | ЭГРЭС-1 220 | 39 | 360 | 50 | 0 | 0 |  | 1 | TRUE | wye
50 | эгрэс-1 бл3-2 | 50 | 25 | 15 | 0 | 0 |  | 1 | TRUE | wye
51 | эгрэс-1 20 | 51 | 80 | 15 | 0 | 0 |  | 1 | TRUE | wye
60 | эгрэс-2 20 | 60 | 22 | 8 | 0 | 0 |  | 1 | TRUE | wye
63 | Ташкент | 63 | 6964 | 3359 | 0 | 0 |  | 1 | FALSE | wye
130 | ПС-ЦГПП 220 | 130 | 1050 | 98 | 0 | 0 |  | 1 | TRUE | wye
147 | АВРОРА 500 | 147 | 232 | 10 | 0 | 0 |  | 1 | TRUE | wye
175 | Кокшетау | 175 | 255 | 60 | 0 | 0 |  | 1 | TRUE | wye
180 | ПС-ЕГПП | 180 | 103.5 | -99.4 | 0 | 0 |  | 1 | TRUE | wye
224 | Таш.ГРЭС | 224 | 2500 | 0 | 0 | 0 |  | 1 | TRUE | wye
241 | У-К | 241 | 840 | 183 | 0 | 0 |  | 1 | TRUE | wye
306 | Оскаровка 220 | 306 | 20.5 | 5.1 | 0 | 0 |  | 1 | TRUE | wye
310 | Нура 220 | 310 | 67 | 20 | 0 | 0 |  | 1 | TRUE | wye
356 | Кар.ГРЭС-2 110 | 356 | 394 | 152 | 0 | 0 |  | 1 | TRUE | wye
455 | Кумколь 110 | 455 | 80.6 | 35.1 | 0 | 0 |  | 1 | TRUE | wye
465 | Каражал 220 | 465 | 33 | 3.2 | 0 | 0 |  | 1 | TRUE | wye
466 | Жезказган 220 | 466 | 130 | 32 | 0 | 0 |  | 1 | TRUE | wye
469 | Агадырь | 469 | 10 | 0 | 0 | 0 |  | 1 | TRUE | wye
472 | Балхашская 110 | 472 | 222 | 44.7 | 0 | 0 |  | 1 | TRUE | wye
475 | Мойынты | 475 | 6.4 | 2.1 | 0 | 0 |  | 1 | TRUE | wye
576 | Сокол | 576 | 304 | -25 | 0 | 0 |  | 1 | TRUE | wye
577 | Житикара | 577 | 256 | -33.8 | 0 | 0 |  | 1 | TRUE | wye
590 | Костанай | 590 | 154 | 55 | 0 | 0 |  | 1 | TRUE | wye
801 | Жамбыл 220 | 801 | 265 | 20 | 0 | 0 |  | 1 | TRUE | wye
805 | жгрэс-220 | 805 | 322 | 88 | 0 | 0 |  | 1 | TRUE | wye
814 | Аспара | 814 | 8 | 2 | 0 | 0 |  | 1 | TRUE | wye
831 | Шымкент 220 | 831 | 386.3 | 59.8 | 0 | 0 |  | 1 | TRUE | wye
839 | Жылга | 839 | 11.3 | 4.5 | 0 | 0 |  | 1 | TRUE | wye
840 | Кентау | 840 | 20 | 4 | 0 | 0 |  | 1 | TRUE | wye
842 | Миргалимсай | 842 | 30 | 9.1 | 0 | 0 |  | 1 | TRUE | wye
843 | Шымкентская | 843 | 195.3 | 45.3 | 0 | 0 |  | 1 | TRUE | wye
862 | Кызылорда 220 | 862 | 154 | 44 | 0 | 0 |  | 1 | TRUE | wye
865 | Жанакорган | 865 | 18 | 3 | 0 | 0 |  | 1 | TRUE | wye
869 | Ру-6 | 869 | 18 | 6 | 0 | 0 |  | 1 | TRUE | wye
901 | ЮкГрэс 220 | 901 | 3 | 2 | 0 | 0 |  | 1 | TRUE | wye
903 | Алматы 220 | 903 | 80 | 67.2 | 0 | 0 |  | 1 | TRUE | wye
905 | АТЭЦ-3 110 | 905 | 220 | 50 | 0 | 0 |  | 1 | TRUE | wye
907 | Робот | 907 | 55.7 | 14 | 0 | 0 |  | 1 | TRUE | wye
911 | Чилик | 911 | 50 | 15 | 0 | 0 |  | 1 | TRUE | wye
913 | ПС-7 АХБК 110 | 913 | 670 | 279 | 0 | 0 |  | 1 | TRUE | wye
918 | Западная 220 | 918 | 81.4 | 12.2 | 0 | 0 |  | 1 | TRUE | wye
928 | Медео | 928 | 40 | 12 | 0 | 0 |  | 1 | TRUE | wye
932 | Шу 220 | 932 | 12 | 2 | 0 | 0 |  | 1 | TRUE | wye
953 | Коян-Кос | 953 | 12 | 2 | 0 | 0 |  | 1 | TRUE | wye
981 | Семей 220 | 981 | 180 | 50 | 0 | 0 |  | 1 | TRUE | wye
988 | Талдыкорган 220 | 988 | 202 | 27 | 0 | 0 |  | 1 | TRUE | wye
1621 | Рубцовск | 1621 | 175 | 79 | 0 | 0 |  | 1 | TRUE | wye
1630 | Барнаул | 1630 | 368 | 60 | 0 | 0 |  | 1 | TRUE | wye
1631 | Заря | 1631 | 5 | 165 | 0 | 0 |  | 1 | TRUE | wye
1636 | Генерация Сибири | 1636 | 2754 | 200 | 0 | 0 |  | 1 | TRUE | wye
1817 | ТАВРИЧЕСКАЯ | 1817 | 385 | 114 | 0 | 0 |  | 1 | TRUE | wye
1850 | ИРТЫШСКАЯ | 1850 | 174 | 11 | 0 | 0 |  | 1 | TRUE | wye
1852 | Витязь | 1852 | 1 | 1 | 0 | 0 |  | 1 | TRUE | wye
1853 | Восход | 1853 | 178 | 40 | 0 | 0 |  | 1 | TRUE | wye
1916 | Главная 220 | 1916 | 825 | 102 | 0 | 0 |  | 1 | TRUE | wye
2918 | Фрунзе 220 | 2918 | 195 | 25 | 0 | 0 |  | 1 | TRUE | wye
2921 | ГЕНЕРАЦИЯ ЦА-1 | 2921 | 2295 | 25 | 0 | 0 |  | 1 | TRUE | wye
2925 | ТашкентТэс 220 | 2925 | 660 | 70 | 0 | 0 |  | 1 | TRUE | wye
2952 | Кемин 220 | 2952 | 420 | 76.2 | 0 | 0 |  | 1 | TRUE | wye
4703 | Козырево | 4703 | 140 | -35 | 0 | 0 |  | 1 | TRUE | wye
4705 | Челябинск | 4705 | 716 | -196 | 0 | 0 |  | 1 | TRUE | wye
4727 | Курган | 4727 | 16 | 55 | 0 | 0 |  | 1 | TRUE | wye
4785 | Магнитагорская | 4785 | 584.8 | 40 | 0 | 0 |  | 1 | TRUE | wye
4799 | Троицская ГРЭС | 4799 | 280 | 66.7 | 0 | 0 |  | 1 | TRUE | wye
7201 | пр/уз. Семей У-К | 7201 | 135 | 40 | 0 | 0 |  | 1 | TRUE | wye
7202 | пр/уз. ЕЭК Семей | 7202 | 24 | 9 | 0 | 0 |  | 1 | TRUE | wye
7203 | пр/уз. Эгрэс-1 ЕЭК | 7203 | 173 | 49.7 | 0 | 0 |  | 1 | TRUE | wye
7204 | пр/уз.ЦГПП-ЭГРЭС-1 | 7204 | 38 | 18.8 | 0 | 0 |  | 1 | TRUE | wye
7205 | пр/уз.ЦГПП-Осакоровка | 7205 | 9.1 | 1.3 | 0 | 0 |  | 1 | TRUE | wye
7206 | пр/уз.ЭГРЭС 1 Осакоровка | 7206 | 54 | 30.4 | 0 | 0 |  | 1 | TRUE | wye
7208 | пр/уз.КарГРЭС-Нура | 7208 | 1183.4 | 452.2 | 0 | 0 |  | 1 | TRUE | wye
7209 | пр/уз.Каргрэс-Каражал | 7209 | 7.4 | 2.4 | 0 | 0 |  | 1 | TRUE | wye
7210 | пр/уз.Каргрэс-Агадырь | 7210 | 20.3 | 7.9 | 0 | 0 |  | 1 | TRUE | wye
7211 | пр/уз.Каргрэс - Балхашская | 7211 | 18 | 5.3 | 0 | 0 |  | 1 | TRUE | wye
7212 | пр/уз ЮкГРЭС ШУ | 7212 | 15 | 4.6 | 0 | 0 |  | 1 | TRUE | wye
7213 | пр/уз Алматы Алма | 7213 | 305 | 90 | 0 | 0 |  | 1 | TRUE | wye
7214 | пр/уз Главная Кемин | 7214 | 320 | 15 | 0 | 0 |  | 1 | TRUE | wye
7216 | пр/уз Жамбыл Шымкент | 7216 | 55.1 | 16.2 | 0 | 0 |  | 1 | TRUE | wye
7217 | пр/уз ГлавнаяФрунзе | 7217 | 175 | 30 | 0 | 0 |  | 1 | TRUE | wye
7218 | пр/уз ТалдыкорганРобот | 7218 | 38.9 | 5 | 0 | 0 |  | 1 | TRUE | wye
7219 | пр/уз МойынтыЮкгрэс | 7219 | 13 | 4.2 | 0 | 0 |  | 1 | TRUE | wye
7221 | пр/уз ЖезказганКаражал | 7221 | 207 | 42.9 | 0 | 0 |  | 1 | TRUE | wye
7223 | пр/уз жгрэс- Фрунзе | 7223 | 14 | 2 | 0 | 0 |  | 1 | TRUE | wye
7224 | пр/уз Кентау Жамбыл 220 | 7224 | 43 | 6.3 | 0 | 0 |  | 1 | TRUE | wye
7225 | Пр/уз Шымкент-220/Жылга | 7225 | 29.9 | 7.7 | 0 | 0 |  | 1 | TRUE | wye
7226 | пр/уз Ру-6/Кызылорда | 7226 | 20 | 3 | 0 | 0 |  | 1 | TRUE | wye
7227 | пр/уз Кызылорда-Кумколь | 7227 | 93 | -10 | 0 | 0 |  | 1 | TRUE | wye
7228 | ГНПС | 7228 | 20 | 3.4 | 0 | 0 |  | 1 | TRUE | wye
7229 | пр/уз Кар.ГРЭС-2 - Осакоровка | 7229 | 24 | 19.3 | 0 | 0 |  | 1 | TRUE | wye
9917 | Барабинская | 9917 | 146.3 | -42.2 | 0 | 0 |  | 1 | TRUE | wye

## gen
| name | bus | p_mw | vm_pu | sn_mva | min_q_mvar | max_q_mvar | scaling | slack | in_service | slack_weight | type | power_station_trafo
30 | еэк-20-бл5-8 | 30 | 809 | 1 |  | -163 | 573 | 1 | FALSE | TRUE | 0
33 | ПС-ЕЭК 220 | 33 | 1120 | 1.0727 |  | -150 | 804 | 1 | FALSE | TRUE | 0
50 | эгрэс-1 бл3-2 | 50 | 501 | 1 |  | -130 | 340 | 1 | FALSE | TRUE | 0
51 | эгрэс-1 20 | 51 | 2896 | 1 |  | -430 | 1880 | 1 | FALSE | TRUE | 0
60 | эгрэс-2 20 | 60 | 961 | 1 |  | -500 | 800 | 1 | FALSE | TRUE | 0
63 | Ташкент | 63 | 7018 | 1.014 |  | -2300 | 11500 | 1 | FALSE | FALSE | 0
130 | ПС-ЦГПП 220 | 130 | 468 | 1.0818 |  | 40 | 250 | 1 | FALSE | TRUE | 0
147 | АВРОРА 500 | 147 | 250 | 1.01 |  | -64 | 152 | 1 | FALSE | TRUE | 0
224 | Таш.ГРЭС | 224 | 2934 | 1.02 |  | -1000 | 1000 | 1 | FALSE | TRUE | 0
241 | У-К | 241 | 1301 | 1.05 |  | -383 | 896 | 1 | FALSE | TRUE | 0
356 | Кар.ГРЭС-2 110 | 356 | 577 | 1.1 |  | 35 | 140 | 1 | FALSE | TRUE | 0
455 | Кумколь 110 | 455 | 96 | 1.1 |  | -16.2 | 60.6 | 1 | FALSE | TRUE | 0
466 | Жезказган 220 | 466 | 206 | 1.0682 |  | 25 | 232.5 | 1 | FALSE | TRUE | 0
472 | Балхашская 110 | 472 | 143 | 1.1 |  | -30 | 88 | 1 | FALSE | TRUE | 0
576 | Сокол | 576 | 94 | 1 |  |  |  | 1 | FALSE | TRUE | 0
805 | жгрэс-220 | 805 | 470 | 1.0545 |  | 120 | 422 | 1 | FALSE | TRUE | 0
831 | Шымкент 220 | 831 | 127 | 1.0773 |  |  | 100 | 1 | FALSE | TRUE | 0
862 | Кызылорда 220 | 862 | 53 | 1 |  | -24 | 76 | 1 | FALSE | TRUE | 0
905 | АТЭЦ-3 110 | 905 | 182 | 1.1 |  | 20 | 160 | 1 | FALSE | TRUE | 0
907 | Робот | 907 | 177 | 1.0727 |  |  | 168 | 1 | FALSE | TRUE | 0
913 | ПС-7 АХБК 110 | 913 | 579 | 1.1 |  | 92 | 437 | 1 | FALSE | TRUE | 0
935 | Мойнакская ГЭС | 935 | 78 | 1.1136 |  | -12 | 101 | 1 | FALSE | TRUE | 0
939 | Алма 220 | 939 | 15 | 1.0227 |  | -10 | 10 | 1 | FALSE | TRUE | 0
981 | Семей 220 | 981 | 10 | 1.0773 |  |  |  | 1 | FALSE | TRUE | 0
988 | Талдыкорган 220 | 988 | 36 | 1.0455 |  |  |  | 1 | FALSE | TRUE | 0
1630 | Барнаул | 1630 | 203 | 1.01 |  |  |  | 1 | FALSE | TRUE | 0
1631 | Заря | 1631 | 190 | 1 |  |  |  | 1 | FALSE | TRUE | 0
1636 | Генерация Сибири | 1636 | 3107 | 1.016 |  | -1000 | 1000 | 1 | FALSE | TRUE | 0
1916 | Главная 220 | 1916 | 430 | 1.0045 |  | -100 | 100 | 1 | FALSE | TRUE | 0
2921 | ГЕНЕРАЦИЯ ЦА-1 | 2921 | 2520 | 1.02 |  | -800 | 800 | 1 | FALSE | TRUE | 0
2925 | ТашкентТэс 220 | 2925 | 776 | 1.0455 |  | -500 | 920 | 1 | FALSE | TRUE | 0
2952 | Кемин 220 | 2952 | 450.3 | 1.0455 |  | -160 | 300 | 1 | FALSE | TRUE | 0
4703 | Козырево | 4703 | 558 | 1 |  |  |  | 1 | FALSE | TRUE | 0
4727 | Курган | 4727 | 696 | 1 |  |  |  | 1 | FALSE | TRUE | 0
4782 | Шагол | 4782 | 439 | 1 |  |  |  | 1 | FALSE | TRUE | 0
4799 | Троицская ГРЭС | 4799 | 46 | 1 |  | -500 | 500 | 1 | FALSE | TRUE | 0
7201 | пр/уз. Семей У-К | 7201 | 153 | 1 |  | -35 | 85 | 1 | FALSE | TRUE | 0
7203 | пр/уз. Эгрэс-1 ЕЭК | 7203 | 12 | 1 |  |  | 9 | 1 | FALSE | TRUE | 0
7204 | пр/уз.ЦГПП-ЭГРЭС-1 | 7204 | 30 | 1 |  |  |  | 1 | FALSE | TRUE | 0
7208 | пр/уз.КарГРЭС-Нура | 7208 | 946 | 1.0591 |  | 113.9 | 718.8 | 1 | FALSE | TRUE | 0
7226 | пр/уз Ру-6/Кызылорда | 7226 | 13 | 1 |  |  |  | 1 | FALSE | TRUE | 0
10000 | ЮжУГРЭС | 10000 | 550 | 1.02 |  | -300 | 300 | 1 | FALSE | TRUE | 0

## shunt
| bus | name | q_mvar | p_mw | vn_kv | step | max_step | in_service
25 | 25 | ЭГРЭС-1 | 519.6328 | 0 | 515.0282 | 1 | 1 | FALSE
26 | 26 | ЭК-1150 | 1023.4796 | 0 | 514.794 | 1 | 1 | FALSE
31 | 31 | ЕЭК | 168.6713 | 0 | 508.2343 | 1 | 1 | FALSE
129 | 129 | ЦГПП | 173.3662 | 0 | 515.2591 | 1 | 1 | FALSE
147 | 147 | АВРОРА 500 | 335.8995 | 0 | 507.1461 | 1 | 1 | FALSE
175 | 175 | Кокшетау | 334.9138 | 0 | 511.9189 | 1 | 1 | FALSE
180 | 180 | ПС-ЕГПП | 328.2522 | 0 | 501.3399 | 1 | 1 | FALSE
469 | 469 | Агадырь | 351.7855 | 0 | 519 | 1 | 1 | FALSE
480 | 480 | ЖЕЗКАЗГАН | 179.8351 | 0 | 524.7841 | 1 | 1 | FALSE
576 | 576 | Сокол | 170.0426 | 0 | 510.2962 | 1 | 1 | FALSE
577 | 577 | Житикара | 171.604 | 0 | 512.6337 | 1 | 1 | FALSE
590 | 590 | Костанай | 341.0197 | 0 | 510.9968 | 1 | 1 | FALSE
800 | 800 | Жамбыл | 171.5975 | 0 | 512.624 | 1 | 1 | FALSE
869 | 869 | Ру-6 | 19.5566 | 0 | 227.4277 | 1 | 1 | FALSE
900 | 900 | ЮКГРЭС | 354.5019 | 0 | 521 | 1 | 1 | FALSE
902 | 902 | Алматы | 175.5981 | 0 | 518.5651 | 1 | 1 | FALSE
938 | 938 | Алма | 177.251 | 0 | 521 | 1 | 1 | FALSE
980 | 980 | Семей | 169.2077 | 0 | 509.0419 | 1 | 1 | FALSE
986 | 986 | Актогай | 167.93 | 0 | 507.1163 | 1 | 1 | FALSE
1621 | 1621 | Рубцовск | 332.8544 | 0 | 504.8421 | 1 | 1 | FALSE
1630 | 1630 | Барнаул | 504.1153 | 0 | 507.28 | 1 | 1 | FALSE
1631 | 1631 | Заря | 171.795 | 0 | 512.9188 | 1 | 1 | FALSE
1660 | 1660 | Алтай | 498.076 | 0 | 507.8748 | 1 | 1 | FALSE
1817 | 1817 | ТАВРИЧЕСКАЯ | 170.4354 | 0 | 510.8852 | 1 | 1 | FALSE
1850 | 1850 | ИРТЫШСКАЯ | 168.3533 | 0 | 507.755 | 1 | 1 | FALSE
1852 | 1852 | Витязь | 168.0635 | 0 | 507.3178 | 1 | 1 | FALSE
1853 | 1853 | Восход | 169.8453 | 0 | 510 | 1 | 1 | FALSE
2919 | 2919 | Фрунзе | 171.9975 | 0 | 513.2211 | 1 | 1 | FALSE
2921 | 2921 | ГЕНЕРАЦИЯ ЦА-1 | 169.8453 | 0 | 510 | 1 | 1 | FALSE
4703 | 4703 | Козырево | 170.8056 | 0 | 511.4398 | 1 | 1 | FALSE
4705 | 4705 | Челябинск | 174.2931 | 0 | 516.6346 | 1 | 1 | FALSE
4727 | 4727 | Курган | 339.1735 | 0 | 509.6117 | 1 | 1 | FALSE
4790 | 4790 | Ириклинская ГРЭС | 173.8652 | 0 | 516 | 1 | 1 | FALSE
7227 | 7227 | пр/уз Кызылорда-Кумколь | 34.8007 | 0 | 214.5239 | 1 | 1 | FALSE
9917 | 9917 | Барабинская | 174.5397 | 0 | 517 | 1 | 1 | FALSE
9932 | 9932 | ЧУ | 173.4517 | 0 | 515.3861 | 1 | 1 | FALSE

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
4790 | BAZA | 4790 | 1.032 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
12531 | ЭГРЭС-1 - ЕЭК |  | 25 | 31 | 1 | 3.05 | 36.64 | 1.4732 | 0 | 217.4142 | 1 | 1 | ol | TRUE
225129 | ЭГРЭС-1 - ЦГПП |  | 25 | 129 | 1 | 7.3 | 89.75 | 3.3796 | 0 | 745.1023 | 1 | 1 | ol | TRUE
325325 | ЭГРЭС-1 - Нура |  | 25 | 325 | 1 | 8.3 | 78.3 | 3.3424 | 0 | 1133.7235 | 1 | 1 | ol | TRUE
4251817 | ЭГРЭС-1 - ТАВРИЧЕСКАЯ |  | 25 | 1817 | 1 | 11.8 | 108.2 | 4.5838 | 0 | 440.698 | 1 | 1 | ol | TRUE
62625 | ЭК-1150 - ЭГРЭС-1 |  | 26 | 25 | 1 | 0.25 | 3.15 | 0.12637 | 0 | 482.7278 | 1 | 1 | ol | TRUE
52625 | ЭК-1150 - ЭГРЭС-1 |  | 26 | 25 | 1 | 0.31 | 3.81 | 0.15311 | 0 | 399.0779 | 1 | 1 | ol | TRUE
726175 | ЭК-1150 - Кокшетау |  | 26 | 175 | 1 | 6.05 | 132.7 | 6.9648 | 0 | 608.979 | 1 | 1 | ol | TRUE
826469 | ЭК-1150 - Агадырь |  | 26 | 469 | 1 | 11.6 | 138.3 | 5.5941 | 0 | 1064.1459 | 1 | 1 | ol | TRUE
9261660 | ЭК-1150 - Алтай |  | 26 | 1660 | 1 | 14.79 | 212.33 | 9.123 | 0 | 440.0701 | 1 | 1 | ol | TRUE
102826 | ЭГРЕС-2 500 - ЭК-1150 |  | 28 | 26 | 1 | 0.81 | 11.75 | 0.3301 | 0 | 520.5556 | 1 | 1 | ol | TRUE
112826 | ЭГРЕС-2 500 - ЭК-1150 |  | 28 | 26 | 1 | 0.93 | 11.27 | 0.31291 | 0 | 541.7613 | 1 | 1 | ol | TRUE
12311621 | ЕЭК - Рубцовск |  | 31 | 1621 | 1 | 10.25 | 98.5 | 4.1063 | 0 | 247.1768 | 1 | 1 | ol | TRUE
13311850 | ЕЭК - ИРТЫШСКАЯ |  | 31 | 1850 | 1 | 7.62 | 76.8 | 3.0336 | 0 | 499.2597 | 1 | 1 | ol | TRUE
14337202 | ПС-ЕЭК 220 - пр/уз. ЕЭК Семей |  | 33 | 7202 | 1 | 4.94 | 52.48 | 2.0181 | 0 | 292.1162 | 1 | 1 | ol | TRUE
15337203 | ПС-ЕЭК 220 - пр/уз. Эгрэс-1 ЕЭК |  | 33 | 7203 | 1 | 4.43 | 18.775 | 1.7482 | 0 | 462.505 | 1 | 1 | ol | TRUE
16397203 | ЭГРЭС-1 220 - пр/уз. Эгрэс-1 ЕЭК |  | 39 | 7203 | 1 | 4.43 | 18.775 | 1.7482 | 0 | 67.0137 | 1 | 1 | ol | TRUE
17397204 | ЭГРЭС-1 220 - пр/уз.ЦГПП-ЭГРЭС-1 |  | 39 | 7204 | 1 | 13.62 | 60.625 | 2.0482 | 0 | 329.4184 | 1 | 1 | ol | TRUE
18397206 | ЭГРЭС-1 220 - пр/уз.ЭГРЭС 1 Осакоровка |  | 39 | 7206 | 1 | 17.395 | 68.48 | 1.4039 | 0 | 349.7053 | 1 | 1 | ol | TRUE
19129180 | ЦГПП - ПС-ЕГПП |  | 129 | 180 | 1 | 11.12 | 113.36 | 4.5488 | 0 | 289.2492 | 1 | 1 | ol | TRUE
201307204 | ПС-ЦГПП 220 - пр/уз.ЦГПП-ЭГРЭС-1 |  | 130 | 7204 | 1 | 13.62 | 60.625 | 2.0482 | 0 | 299.4027 | 1 | 1 | ol | TRUE
211307205 | ПС-ЦГПП 220 - пр/уз.ЦГПП-Осакоровка |  | 130 | 7205 | 1 | 2.865 | 11.525 | 2.0646 | 0 | 169.6706 | 1 | 1 | ol | TRUE
221471817 | АВРОРА 500 - ТАВРИЧЕСКАЯ |  | 147 | 1817 | 1 | 11.47 | 87.78 | 3.4378 | 0 | 221.7121 | 1 | 1 | ol | TRUE
231474727 | АВРОРА 500 - Курган |  | 147 | 4727 | 1 | 9.37 | 84.1 | 3.1959 | 0 | 237.8429 | 1 | 1 | ol | TRUE
24175147 | Кокшетау - АВРОРА 500 |  | 175 | 147 | 1 | 5 | 49.9 | 1.9513 | 0 | 399.9037 | 1 | 1 | ol | TRUE
25175590 | Кокшетау - Костанай |  | 175 | 590 | 1 | 5.02 | 106.96 | 5.561 | 0 | 647.736 | 1 | 1 | ol | TRUE
26180576 | ПС-ЕГПП - Сокол |  | 180 | 576 | 1 | 8.8 | 80 | 3.3996 | 0 | 10 | 1 | 1 | ol | FALSE
2722463 | Таш.ГРЭС - Ташкент |  | 224 | 63 | 1 | 0.45 | 5.81 | 0.20691 | 0 | 10 | 1 | 1 | ol | FALSE
28224830 | Таш.ГРЭС - Шымкент |  | 224 | 830 | 1 | 3 | 32.5 | 1.4484 | 0 | 420.6407 | 1 | 1 | ol | TRUE
292417201 | У-К - пр/уз. Семей У-К |  | 241 | 7201 | 1 | 3.075 | 24.27 | 1.9035 | 0 | 314.6409 | 1 | 1 | ol | TRUE
303067205 | Оскаровка 220 - пр/уз.ЦГПП-Осакоровка |  | 306 | 7205 | 1 | 2.86 | 11.52 | 2.0646 | 0 | 159.7863 | 1 | 1 | ol | TRUE
313067206 | Оскаровка 220 - пр/уз.ЭГРЭС 1 Осакоровка |  | 306 | 7206 | 1 | 17.395 | 68.48 | 1.4039 | 0 | 241.2247 | 1 | 1 | ol | TRUE
323067229 | Оскаровка 220 - пр/уз Кар.ГРЭС-2 - Осакоровка |  | 306 | 7229 | 1 | 8.88 | 38.87 | 0.76142 | 0 | 262.7601 | 1 | 1 | ol | TRUE
333107208 | Нура 220 - пр/уз.КарГРЭС-Нура |  | 310 | 7208 | 1 | 2.68 | 10.525 | 0.85787 | 0 | 617.2467 | 1 | 1 | ol | TRUE
34325469 | Нура - Агадырь |  | 325 | 469 | 1 | 6.86 | 79.4 | 3.1864 | 0 | 793.0665 | 1 | 1 | ol | TRUE
353557208 | Кар.ГРЭС-2 - пр/уз.КарГРЭС-Нура |  | 355 | 7208 | 1 | 2.68 | 10.52 | 0.85787 | 0 | 40.8868 | 1 | 1 | ol | TRUE
363557209 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Каражал |  | 355 | 7209 | 1 | 12.8 | 51.65 | 0.99714 | 0 | 274.7 | 1 | 1 | ol | TRUE
373557210 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Агадырь |  | 355 | 7210 | 1 | 9.005 | 36.565 | 0.73261 | 0 | 223.7213 | 1 | 1 | ol | TRUE
383557211 | Кар.ГРЭС-2 - пр/уз.Каргрэс - Балхашская |  | 355 | 7211 | 1 | 20.28 | 81.25 | 1.5873 | 0 | 167.5425 | 1 | 1 | ol | TRUE
393557229 | Кар.ГРЭС-2 - пр/уз Кар.ГРЭС-2 - Осакоровка |  | 355 | 7229 | 1 | 3.53 | 15.44 | 0.3024 | 0 | 208.9962 | 1 | 1 | ol | TRUE
40465468 | Каражал 220 - Агадырь 220 |  | 465 | 468 | 1 | 16.4 | 71.77 | 1.4059 | 0 | 180.3915 | 1 | 1 | ol | TRUE
414657209 | Каражал 220 - пр/уз.Каргрэс-Каражал |  | 465 | 7209 | 1 | 12.8 | 51.65 | 0.99714 | 0 | 245.8543 | 1 | 1 | ol | TRUE
424657221 | Каражал 220 - пр/уз ЖезказганКаражал |  | 465 | 7221 | 1 | 7.68 | 29.92 | 2.7445 | 0 | 315.5342 | 1 | 1 | ol | TRUE
43466467 | Жезказган 220 - Кумколь 220 |  | 466 | 467 | 1 | 11.606 | 48.977 | 4.0054 | 0 | 416.7978 | 1 | 1 | ol | TRUE
444667221 | Жезказган 220 - пр/уз ЖезказганКаражал |  | 466 | 7221 | 1 | 7.68 | 29.92 | 2.7445 | 0 | 246.0859 | 1 | 1 | ol | TRUE
454677227 | Кумколь 220 - пр/уз Кызылорда-Кумколь |  | 467 | 7227 | 1 | 27.385 | 107.645 | 2.2894 | 0 | 444.3277 | 1 | 1 | ol | TRUE
46468473 | Агадырь 220 - Балхашская |  | 468 | 473 | 1 | 23.67 | 99.68 | 2.0376 | 0 | 82.7528 | 1 | 1 | ol | TRUE
474687210 | Агадырь 220 - пр/уз.Каргрэс-Агадырь |  | 468 | 7210 | 1 | 9.005 | 36.56 | 0.73261 | 0 | 173.1875 | 1 | 1 | ol | TRUE
48469480 | Агадырь - ЖЕЗКАЗГАН |  | 469 | 480 | 1 | 12.6 | 123 | 4.8894 | 0 | 340.0774 | 1 | 1 | ol | TRUE
50469900 | Агадырь - ЮКГРЭС |  | 469 | 900 | 1 | 11.5 | 118.41 | 4.6067 | 0 | 757.3364 | 1 | 1 | ol | TRUE
49469900 | Агадырь - ЮКГРЭС |  | 469 | 900 | 1 | 12.7 | 115.6 | 4.8576 | 0 | 779.2578 | 1 | 1 | ol | TRUE
51473475 | Балхашская - Мойынты |  | 473 | 475 | 1 | 16.46 | 70.14 | 1.4219 | 0 | 54.5325 | 1 | 1 | ol | TRUE
524737211 | Балхашская - пр/уз.Каргрэс - Балхашская |  | 473 | 7211 | 1 | 20.28 | 81.25 | 1.5873 | 0 | 105.7225 | 1 | 1 | ol | TRUE
53475468 | Мойынты - Агадырь 220 |  | 475 | 468 | 1 | 12.8 | 54.2 | 1.1135 | 0 | 84.7989 | 1 | 1 | ol | TRUE
544757219 | Мойынты - пр/уз МойынтыЮкгрэс |  | 475 | 7219 | 1 | 13.245 | 57.565 | 1.1703 | 0 | 10 | 1 | 1 | ol | FALSE
55576577 | Сокол - Житикара |  | 576 | 577 | 1 | 4.7 | 53.5 | 2.1264 | 0 | 565.0733 | 1 | 1 | ol | TRUE
56590576 | Костанай - Сокол |  | 590 | 576 | 1 | 1.3 | 13.6 | 0.50613 | 0 | 645.3939 | 1 | 1 | ol | TRUE
575904705 | Костанай - Челябинск |  | 590 | 4705 | 1 | 4 | 75.3 | 4.5201 | 0 | 316.8833 | 1 | 1 | ol | TRUE
58800830 | Жамбыл - Шымкент |  | 800 | 830 | 1 | 4.1 | 51.6 | 1.9481 | 0 | 129.263 | 1 | 1 | ol | TRUE
59801805 | Жамбыл 220 - жгрэс-220 |  | 801 | 805 | 1 | 1.448 | 5.707 | 1.0342 | 0 | 510.951 | 1 | 1 | ol | TRUE
608017216 | Жамбыл 220 - пр/уз Жамбыл Шымкент |  | 801 | 7216 | 1 | 5.3954 | 21.463 | 1.7633 | 0 | 143.8301 | 1 | 1 | ol | TRUE
61814805 | Аспара - жгрэс-220 |  | 814 | 805 | 1 | 21.9 | 86.36 | 1.8182 | 0 | 182.5791 | 1 | 1 | ol | TRUE
62831843 | Шымкент 220 - Шымкентская |  | 831 | 843 | 1 | 1.72 | 10.75 | 0.24383 | 0 | 272.464 | 1 | 1 | ol | TRUE
638317216 | Шымкент 220 - пр/уз Жамбыл Шымкент |  | 831 | 7216 | 1 | 5.3954 | 21.463 | 1.7633 | 0 | 46.3317 | 1 | 1 | ol | TRUE
648317225 | Шымкент 220 - Пр/уз Шымкент-220/Жылга |  | 831 | 7225 | 1 | 9.98 | 39.675 | 0.82731 | 0 | 44.2969 | 1 | 1 | ol | TRUE
658317228 | Шымкент 220 - ГНПС |  | 831 | 7228 | 1 | 4.15 | 18.15 | 0.35547 | 0 | 164.1601 | 1 | 1 | ol | TRUE
66839843 | Жылга - Шымкентская |  | 839 | 843 | 1 | 6.55 | 41.4 | 0.88907 | 0 | 137.0951 | 1 | 1 | ol | TRUE
678392925 | Жылга - ТашкентТэс 220 |  | 839 | 2925 | 1 | 5.02 | 31.85 | 0.6777 | 0 | 10 | 1 | 1 | ol | FALSE
688397225 | Жылга - Пр/уз Шымкент-220/Жылга |  | 839 | 7225 | 1 | 9.98 | 39.67 | 0.82731 | 0 | 90.7082 | 1 | 1 | ol | TRUE
69840869 | Кентау - Ру-6 |  | 840 | 869 | 1 | 21.97 | 85.81 | 1.8077 | 0 | 111.8196 | 1 | 1 | ol | TRUE
708407224 | Кентау - пр/уз Кентау Жамбыл 220 |  | 840 | 7224 | 1 | 13.389 | 52.2869 | 1.5553 | 0 | 95.2907 | 1 | 1 | ol | TRUE
71842840 | Миргалимсай - Кентау |  | 842 | 840 | 1 | 2.16 | 8.4 | 0.17221 | 0 | 71.6359 | 1 | 1 | ol | TRUE
72842843 | Миргалимсай - Шымкентская |  | 842 | 843 | 1 | 19.7 | 79.3 | 1.5095 | 0 | 142.0375 | 1 | 1 | ol | TRUE
738627226 | Кызылорда 220 - пр/уз Ру-6/Кызылорда |  | 862 | 7226 | 1 | 3.855 | 15.055 | 1.35 | 0 | 188.9488 | 1 | 1 | ol | TRUE
748627227 | Кызылорда 220 - пр/уз Кызылорда-Кумколь |  | 862 | 7227 | 1 | 27.385 | 107.645 | 2.2894 | 0 | 219.0329 | 1 | 1 | ol | TRUE
75865842 | Жанакорган - Миргалимсай |  | 865 | 842 | 1 | 12.53 | 48.14 | 1.0091 | 0 | 116.9431 | 1 | 1 | ol | TRUE
76865869 | Жанакорган - Ру-6 |  | 865 | 869 | 1 | 7.21 | 28.31 | 0.59144 | 0 | 87.1997 | 1 | 1 | ol | TRUE
778697226 | Ру-6 - пр/уз Ру-6/Кызылорда |  | 869 | 7226 | 1 | 3.86 | 15.055 | 1.35 | 0 | 159.8731 | 1 | 1 | ol | TRUE
78900902 | ЮКГРЭС - Алматы |  | 900 | 902 | 1 | 9.35 | 85 | 3.5811 | 0 | 369.0762 | 1 | 1 | ol | TRUE
79900938 | ЮКГРЭС - Алма |  | 900 | 938 | 1 | 9.2 | 98.2 | 3.6543 | 0 | 281.7378 | 1 | 1 | ol | TRUE
809009932 | ЮКГРЭС - ЧУ |  | 900 | 9932 | 1 | 5.2 | 63.6 | 2.5084 | 0 | 761.1166 | 1 | 1 | ol | TRUE
819017212 | ЮкГрэс 220 - пр/уз ЮкГРЭС ШУ |  | 901 | 7212 | 1 | 11.97 | 53.21 | 1.0439 | 0 | 259.9392 | 1 | 1 | ol | TRUE
829017219 | ЮкГрэс 220 - пр/уз МойынтыЮкгрэс |  | 901 | 7219 | 1 | 13.24 | 57.56 | 1.1703 | 0 | 51.4076 | 1 | 1 | ol | TRUE
83902938 | Алматы - Алма |  | 902 | 938 | 1 | 1.8 | 19.5 | 0.72418 | 0 | 364.4418 | 1 | 1 | ol | TRUE
849029932 | Алматы - ЧУ |  | 902 | 9932 | 1 | 7.1 | 72.41 | 2.8999 | 0 | 312.3146 | 1 | 1 | ol | TRUE
85903904 | Алматы 220 - АТЭЦ-3 |  | 903 | 904 | 1 | 7 | 30.15 | 0.61754 | 0 | 71.6076 | 1 | 1 | ol | TRUE
86903907 | Алматы 220 - Робот |  | 903 | 907 | 1 | 7.71 | 33.81 | 0.6621 | 0 | 213.0826 | 1 | 1 | ol | TRUE
87903928 | Алматы 220 - Медео |  | 903 | 928 | 1 | 7.01 | 31.31 | 0.61436 | 0 | 67.8406 | 1 | 1 | ol | TRUE
889037213 | Алматы 220 - пр/уз Алматы Алма |  | 903 | 7213 | 1 | 3.975 | 16.95 | 6.0497 | 0 | 321.7076 | 1 | 1 | ol | TRUE
89904939 | АТЭЦ-3 - Алма 220 |  | 904 | 939 | 1 | 0.75 | 5.35 | 0.45201 | 0 | 661.0078 | 1 | 1 | ol | TRUE
909077218 | Робот - пр/уз ТалдыкорганРобот |  | 907 | 7218 | 1 | 5 | 22.175 | 1.7874 | 0 | 145.0163 | 1 | 1 | ol | TRUE
91912953 | ПС-7 АХБК - Коян-Кос |  | 912 | 953 | 1 | 0.565 | 3.15 | 0.25784 | 0 | 484.7404 | 1 | 1 | ol | TRUE
92918912 | Западная 220 - ПС-7 АХБК |  | 918 | 912 | 1 | 5 | 20 | 0.49021 | 0 | 209.3968 | 1 | 1 | ol | TRUE
939182952 | Западная 220 - Кемин 220 |  | 918 | 2952 | 1 | 9.27 | 40.58 | 0.79484 | 0 | 1211.9598 | 1 | 1 | ol | TRUE
94928904 | Медео - АТЭЦ-3 |  | 928 | 904 | 1 | 0.33 | 1.49 | 0.029285 | 0 | 101.834 | 1 | 1 | ol | TRUE
95932814 | Шу 220 - Аспара |  | 932 | 814 | 1 | 1.3 | 6 | 0.11778 | 0 | 200.144 | 1 | 1 | ol | TRUE
969321916 | Шу 220 - Главная 220 |  | 932 | 1916 | 1 | 16.8 | 72 | 1.4961 | 0 | 576.5124 | 1 | 1 | ol | TRUE
979327212 | Шу 220 - пр/уз ЮкГРЭС ШУ |  | 932 | 7212 | 1 | 11.97 | 53.21 | 1.0439 | 0 | 219.7974 | 1 | 1 | ol | TRUE
98935907 | Мойнакская ГЭС - Робот |  | 935 | 907 | 1 | 17.1 | 95.7 | 1.9577 | 0 | 86.325 | 1 | 1 | ol | TRUE
99935911 | Мойнакская ГЭС - Чилик |  | 935 | 911 | 1 | 7.3 | 40.9 | 0.83718 | 0 | 162.0115 | 1 | 1 | ol | TRUE
100939907 | Алма 220 - Робот |  | 939 | 907 | 1 | 2.1 | 14.2 | 0.2989 | 0 | 282.7102 | 1 | 1 | ol | TRUE
101939911 | Алма 220 - Чилик |  | 939 | 911 | 1 | 12 | 52.7 | 1.0314 | 0 | 78.3916 | 1 | 1 | ol | TRUE
1029397213 | Алма 220 - пр/уз Алматы Алма |  | 939 | 7213 | 1 | 3.975 | 16.95 | 6.0497 | 0 | 507.2153 | 1 | 1 | ol | TRUE
103953904 | Коян-Кос - АТЭЦ-3 |  | 953 | 904 | 1 | 0.425 | 2.375 | 0.19417 | 0 | 509.3247 | 1 | 1 | ol | TRUE
10498026 | Семей - ЭК-1150 |  | 980 | 26 | 1 | 10.1 | 122.52 | 4.8505 | 0 | 397.0908 | 1 | 1 | ol | TRUE
105980240 | Семей - Усть-Каменогорск |  | 980 | 240 | 1 | 5.72 | 58.55 | 2.2944 | 0 | 502.1389 | 1 | 1 | ol | TRUE
106980986 | Семей - Актогай |  | 980 | 986 | 1 | 9.84 | 120.42 | 4.5348 | 0 | 874.9283 | 1 | 1 | ol | TRUE
1079817201 | Семей 220 - пр/уз. Семей У-К |  | 981 | 7201 | 1 | 3.08 | 24.27 | 1.9035 | 0 | 403.1595 | 1 | 1 | ol | TRUE
1089817202 | Семей 220 - пр/уз. ЕЭК Семей |  | 981 | 7202 | 1 | 4.945 | 52.485 | 2.0181 | 0 | 221.8808 | 1 | 1 | ol | TRUE
109986987 | Актогай - Талдыкорган |  | 986 | 987 | 1 | 8.33 | 88.52 | 3.2936 | 0 | 868.5443 | 1 | 1 | ol | TRUE
110987938 | Талдыкорган - Алма |  | 987 | 938 | 1 | 5.91 | 62.76 | 2.3352 | 0 | 535.0456 | 1 | 1 | ol | TRUE
1119887218 | Талдыкорган 220 - пр/уз ТалдыкорганРобот |  | 988 | 7218 | 1 | 5 | 22.175 | 1.7874 | 0 | 245.4457 | 1 | 1 | ol | TRUE
1121621240 | Рубцовск - Усть-Каменогорск |  | 1621 | 240 | 1 | 4.34 | 44.02 | 1.7826 | 0 | 119.241 | 1 | 1 | ol | TRUE
11316301621 | Барнаул - Рубцовск |  | 1630 | 1621 | 1 | 10.3 | 105 | 4.3642 | 0 | 232.6227 | 1 | 1 | ol | TRUE
11416319917 | Заря - Барабинская |  | 1631 | 9917 | 1 | 10.8 | 110 | 4.3785 | 0 | 370.3308 | 1 | 1 | ol | TRUE
11616601630 | Алтай - Барнаул |  | 1660 | 1630 | 1 | 0.19 | 1.97 | 0.078625 | 0 | 238.8781 | 1 | 1 | ol | TRUE
11516601630 | Алтай - Барнаул |  | 1660 | 1630 | 1 | 0.26 | 2.64 | 0.10536 | 0 | 179.6649 | 1 | 1 | ol | TRUE
11716601631 | Алтай - Заря |  | 1660 | 1631 | 1 | 5.46 | 50.12 | 2.1073 | 0 | 180.0566 | 1 | 1 | ol | TRUE
11816601636 | Алтай - Генерация Сибири |  | 1660 | 1636 | 1 | 5 | 120 | 6.0481 | 0 | 478.9998 | 1 | 1 | ol | TRUE
11918171850 | ТАВРИЧЕСКАЯ - ИРТЫШСКАЯ |  | 1817 | 1850 | 1 | 3.42 | 35.28 | 1.3942 | 0 | 304.4337 | 1 | 1 | ol | TRUE
12018521853 | Витязь - Восход |  | 1852 | 1853 | 1 | 8.56 | 102.65 | 4.1502 | 0 | 208.3847 | 1 | 1 | ol | TRUE
12118531817 | Восход - ТАВРИЧЕСКАЯ |  | 1853 | 1817 | 1 | 2.1 | 21.85 | 0.87092 | 0 | 87.465 | 1 | 1 | ol | TRUE
12218539917 | Восход - Барабинская |  | 1853 | 9917 | 1 | 8.43 | 86.95 | 3.462 | 0 | 225.8305 | 1 | 1 | ol | TRUE
1231916903 | Главная 220 - Алматы 220 |  | 1916 | 903 | 1 | 19 | 82 | 1.6712 | 0 | 617.4874 | 1 | 1 | ol | TRUE
12419167214 | Главная 220 - пр/уз Главная Кемин |  | 1916 | 7214 | 1 | 5.82 | 25.065 | 0.51237 | 0 | 495.7157 | 1 | 1 | ol | TRUE
12519167217 | Главная 220 - пр/уз ГлавнаяФрунзе |  | 1916 | 7217 | 1 | 5.55 | 23.35 | 0.67961 | 0 | 366.2026 | 1 | 1 | ol | TRUE
12629187215 | Фрунзе 220 - пр/уз Фрунзе Кемин |  | 2918 | 7215 | 1 | 10.83 | 46.63 | 1.9064 | 0 | 383.5566 | 1 | 1 | ol | TRUE
12729187217 | Фрунзе 220 - пр/уз ГлавнаяФрунзе |  | 2918 | 7217 | 1 | 5.55 | 23.35 | 0.67961 | 0 | 832.7616 | 1 | 1 | ol | TRUE
1282919800 | Фрунзе - Жамбыл |  | 2919 | 800 | 1 | 6 | 69 | 2.5816 | 0 | 319.5887 | 1 | 1 | ol | TRUE
12929192921 | Фрунзе - ГЕНЕРАЦИЯ ЦА-1 |  | 2919 | 2921 | 1 | 7.1 | 64.2 | 2.5848 | 0 | 305.8679 | 1 | 1 | ol | TRUE
1302925843 | ТашкентТэс 220 - Шымкентская |  | 2925 | 843 | 1 | 8.58 | 52.04 | 1.1498 | 0 | 264.4606 | 1 | 1 | ol | TRUE
13129527214 | Кемин 220 - пр/уз Главная Кемин |  | 2952 | 7214 | 1 | 5.82 | 25.065 | 0.51237 | 0 | 472.678 | 1 | 1 | ol | TRUE
13229527215 | Кемин 220 - пр/уз Фрунзе Кемин |  | 2952 | 7215 | 1 | 10.83 | 46.63 | 1.9064 | 0 | 353.6325 | 1 | 1 | ol | TRUE
13347034727 | Козырево - Курган |  | 4703 | 4727 | 1 | 9.02 | 84.65 | 3.3933 | 0 | 592.1819 | 1 | 1 | ol | TRUE
13447034782 | Козырево - Шагол |  | 4703 | 4782 | 1 | 1.96 | 16.2 | 0.69394 | 0 | 1037.6561 | 1 | 1 | ol | TRUE
13547271852 | Курган - Витязь |  | 4727 | 1852 | 1 | 9.4 | 87.42 | 3.547 | 0 | 177.2686 | 1 | 1 | ol | TRUE
13647824705 | Шагол - Челябинск |  | 4782 | 4705 | 1 | 1.5 | 19 | 0.73213 | 0 | 1042.5046 | 1 | 1 | ol | TRUE
137478210000 | Шагол - ЮжУГРЭС |  | 4782 | 10000 | 1 | 1.78 | 25.87 | 1.2781 | 0 | 549.5441 | 1 | 1 | ol | TRUE
13847854799 | Магнитагорская - Троицская ГРЭС |  | 4785 | 4799 | 1 | 6.2 | 54.6 | 2.4351 | 0 | 822.7375 | 1 | 1 | ol | TRUE
1394790577 | Ириклинская ГРЭС - Житикара |  | 4790 | 577 | 1 | 5.05 | 57.9 | 2.3046 | 0 | 295.4819 | 1 | 1 | ol | TRUE
14047904785 | Ириклинская ГРЭС - Магнитагорская |  | 4790 | 4785 | 1 | 6.8 | 66 | 2.7057 | 0 | 189.8523 | 1 | 1 | ol | TRUE
1414799576 | Троицская ГРЭС - Сокол |  | 4799 | 576 | 1 | 4.92 | 50 | 1.9799 | 0 | 200.6079 | 1 | 1 | ol | TRUE
1427223805 | пр/уз жгрэс- Фрунзе - жгрэс-220 |  | 7223 | 805 | 1 | 9.885 | 37.125 | 0.82142 | 0 | 131.544 | 1 | 1 | ol | TRUE
14372232918 | пр/уз жгрэс- Фрунзе - Фрунзе 220 |  | 7223 | 2918 | 1 | 9.885 | 37.125 | 0.82142 | 0 | 163.1285 | 1 | 1 | ol | TRUE
1447224801 | пр/уз Кентау Жамбыл 220 - Жамбыл 220 |  | 7224 | 801 | 1 | 13.389 | 52.2869 | 1.5553 | 0 | 209.4548 | 1 | 1 | ol | TRUE
1457228840 | ГНПС - Кентау |  | 7228 | 840 | 1 | 20.27 | 88.72 | 1.7379 | 0 | 116.6029 | 1 | 1 | ol | TRUE
14699322919 | ЧУ - Фрунзе |  | 9932 | 2919 | 1 | 2.82 | 28.85 | 1.1523 | 0 | 788.3941 | 1 | 1 | ol | TRUE
147100004799 | ЮжУГРЭС - Троицская ГРЭС |  | 10000 | 4799 | 1 | 1.29 | 18.64 | 0.96483 | 0 | 1202.5117 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service | pt_percent | oltc | Unnamed: 26 | Unnamed: 27
12539 | ЭГРЭС-1 - ЭГРЭС-1 220 |  | 25 | 39 | 801 | 500 | 220 | 8.6 | 0.025121 | 297.45 | 0.15 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
22551 | ЭГРЭС-1 - эгрэс-1 20 |  | 25 | 51 | 630 | 525 | 20 | 14.2 | 0.20386 | 270.97 | 0.058 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 3
32860 | ЭГРЕС-2 500 - эгрэс-2 20 |  | 28 | 60 | 630 | 525 | 20 | 14.7 | 0.20317 | 380 | 0.21 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 2
43130 | ЕЭК - еэк-20-бл5-8 |  | 31 | 30 | 400 | 525 | 20 | 12.6 | 0.20075 | 370 | 0.54 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 2
53133 | ЕЭК - ПС-ЕЭК 220 |  | 31 | 33 | 801 | 500 | 237 | 11.9 | 0.17066 | 273.3 | 0.291 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
63950 | ЭГРЭС-1 220 - эгрэс-1 бл3-2 |  | 39 | 50 | 630 | 242 | 20 | 12.5 | 0.20635 | 380 | 0.35 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
7129130 | ЦГПП - ПС-ЦГПП 220 |  | 129 | 130 | 501 | 525 | 230 | 11 | 0.14781 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
8129130 | ЦГПП - ПС-ЦГПП 220 |  | 129 | 130 | 501 | 525 | 230 | 11 | 0.14781 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
92242925 | Таш.ГРЭС - ТашкентТэс 220 |  | 224 | 2925 | 500 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
10240241 | Усть-Каменогорск - У-К |  | 240 | 241 | 500 | 500 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
11240241 | Усть-Каменогорск - У-К |  | 240 | 241 | 500 | 500 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
12325310 | Нура - Нура 220 |  | 325 | 310 | 500 | 500 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
13355356 | Кар.ГРЭС-2 - Кар.ГРЭС-2 110 |  | 355 | 356 | 240 | 242 | 121 | 12.3 | 0.28667 | 452 | 3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 2
14467455 | Кумколь 220 - Кумколь 110 |  | 467 | 455 | 125 | 220 | 110 | 11 | 0.252 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
15469468 | Агадырь - Агадырь 220 |  | 469 | 468 | 500 | 500 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
16473472 | Балхашская - Балхашская 110 |  | 473 | 472 | 125 | 230 | 121 | 11 | 0.252 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 2
17480466 | ЖЕЗКАЗГАН - Жезказган 220 |  | 480 | 466 | 500 | 500 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
18800801 | Жамбыл - Жамбыл 220 |  | 800 | 801 | 501 | 525 | 230 | 10.5 | 0.060413 | 206.49 | 0.35 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
19830831 | Шымкент - Шымкент 220 |  | 830 | 831 | 501 | 525 | 230 | 9.66 | 0.062535 | 306 | 0.92 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
20830831 | Шымкент - Шымкент 220 |  | 830 | 831 | 501 | 525 | 230 | 9.66 | 0.062535 | 306 | 0.92 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
21900901 | ЮКГРЭС - ЮкГрэс 220 |  | 900 | 901 | 500 | 525 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
22902903 | Алматы - Алматы 220 |  | 902 | 903 | 500 | 525 | 230 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
23902903 | Алматы - Алматы 220 |  | 902 | 903 | 500 | 525 | 230 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
24904905 | АТЭЦ-3 - АТЭЦ-3 110 |  | 904 | 905 | 240 | 230 | 121 | 20 | 0.526 | 450 | 3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
25912913 | ПС-7 АХБК - ПС-7 АХБК 110 |  | 912 | 913 | 250 | 230 | 121 | 11 | 0.208 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
26938939 | Алма - Алма 220 |  | 938 | 939 | 501 | 525 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
27938939 | Алма - Алма 220 |  | 938 | 939 | 501 | 525 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
28980981 | Семей - Семей 220 |  | 980 | 981 | 500 | 525 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
29987988 | Талдыкорган - Талдыкорган 220 |  | 987 | 988 | 501 | 525 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
3029192918 | Фрунзе - Фрунзе 220 |  | 2919 | 2918 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
3129192918 | Фрунзе - Фрунзе 220 |  | 2919 | 2918 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1
329932932 | ЧУ - Шу 220 |  | 9932 | 932 | 501 | 525 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1

## measurement
| name | measurement_type | element_type | element | value | std_dev | side
25 | ЭГРЭС-1 | v | bus | 25 | 1.036 | 0.051802
26 | ЭК-1150 | v | bus | 26 | 1.0413 | 0.052067
28 | ЭГРЕС-2 500 | v | bus | 28 | 1.0343 | 0.051716
31 | ЕЭК | v | bus | 31 | 1.0243 | 0.051213
33 | ПС-ЕЭК 220 | v | bus | 33 | 1.0468 | 0.052341
39 | ЭГРЭС-1 220 | v | bus | 39 | 1.0509 | 0.052543
129 | ЦГПП | v | bus | 129 | 1.0349 | 0.051747
130 | ПС-ЦГПП 220 | v | bus | 130 | 1.0974 | 0.05487
147 | АВРОРА 500 | v | bus | 147 | 1.0308 | 0.051541
175 | Кокшетау | v | bus | 175 | 1.0084 | 0.050422
180 | ПС-ЕГПП | v | bus | 180 | 1.0221 | 0.051107
240 | Усть-Каменогорск | v | bus | 240 | 1.023 | 0.051148
241 | У-К | v | bus | 241 | 1.0577 | 0.052884
306 | Оскаровка 220 | v | bus | 306 | 1.0869 | 0.054345
310 | Нура 220 | v | bus | 310 | 1.065 | 0.05325
325 | Нура | v | bus | 325 | 1.039 | 0.051952
355 | Кар.ГРЭС-2 | v | bus | 355 | 1.0532 | 0.052659
465 | Каражал 220 | v | bus | 465 | 1.0136 | 0.050682
466 | Жезказган 220 | v | bus | 466 | 1.0887 | 0.054436
467 | Кумколь 220 | v | bus | 467 | 1.0778 | 0.053889
468 | Агадырь 220 | v | bus | 468 | 1.1029 | 0.055145
469 | Агадырь | v | bus | 469 | 1.0349 | 0.051747
473 | Балхашская | v | bus | 473 | 1.0677 | 0.053386
480 | ЖЕЗКАЗГАН | v | bus | 480 | 1.0354 | 0.05177
576 | Сокол | v | bus | 576 | 1.0322 | 0.05161
577 | ПС 500 кВ Житикара - СШ 500 кВ | v | bus | 577 | 1.0354 | 0.05177
590 | Костанай | v | bus | 590 | 1.0263 | 0.051313
800 | Жамбыл | v | bus | 800 | 1.0016 | 0.05008
801 | Жамбыл 220 | v | bus | 801 | 1.0504 | 0.052518
805 | жгрэс-220 | v | bus | 805 | 1.059 | 0.052948
830 | Шымкент | v | bus | 830 | 0.99382 | 0.049691
831 | Шымкент 220 | v | bus | 831 | 1.0782 | 0.053911
840 | Кентау | v | bus | 840 | 1.0618 | 0.053089
842 | Миргалимсай | v | bus | 842 | 1.0528 | 0.052639
843 | Шымкентская | v | bus | 843 | 1.049 | 0.05245
862 | Кызылорда 220 | v | bus | 862 | 1.0664 | 0.053318
865 | Жанакорган | v | bus | 865 | 1.0667 | 0.053334
869 | Ру-6 | v | bus | 869 | 1.0686 | 0.05343
900 | ЮКГРЭС | v | bus | 900 | 1.0359 | 0.051793
901 | ЮкГрэс 220 | v | bus | 901 | 1.0878 | 0.054391
902 | Алматы | v | bus | 902 | 1.0308 | 0.051541
903 | Алматы 220 | v | bus | 903 | 1.076 | 0.053798
904 | АТЭЦ-3 | v | bus | 904 | 1.0625 | 0.053125
907 | Робот | v | bus | 907 | 1.0605 | 0.053025
912 | ПС-7 АХБК | v | bus | 912 | 1.0195 | 0.050977
918 | Западная 220 | v | bus | 918 | 1.0156 | 0.05078
932 | Шу 220 | v | bus | 932 | 1.0686 | 0.053432
938 | Алма | v | bus | 938 | 1.0435 | 0.052175
939 | Алма 220 | v | bus | 939 | 1.0596 | 0.05298
980 | Семей | v | bus | 980 | 1.0303 | 0.051514
981 | Семей 220 | v | bus | 981 | 1.018 | 0.050902
986 | Актогай | v | bus | 986 | 1.0368 | 0.051839
987 | Талдыкорган | v | bus | 987 | 1.0251 | 0.051256
988 | Талдыкорган 220 | v | bus | 988 | 1.0751 | 0.053755
1621 | Рубцовск | v | bus | 1621 | 1.0418 | 0.052091
1630 | Барнаул | v | bus | 1630 | 1.0275 | 0.051377
1631 | ПС 500 кВ Заря - СШ 500 кВ | v | bus | 1631 | 1.0231 | 0.051157
1660 | Алтай | v | bus | 1660 | 1.0316 | 0.051579
1817 | ТАВРИЧЕСКАЯ | v | bus | 1817 | 1.0301 | 0.051503
1850 | ИРТЫШСКАЯ | v | bus | 1850 | 1.0342 | 0.051709
2925 | ТашкентТэс 220 | v | bus | 2925 | 1.042 | 0.0521
9932 | ЧУ | v | bus | 9932 | 1.0084 | 0.050422
1000001 | эгрэс-1 бл3-2 | p | bus | 50 | 353.72 | 17.686
1000002 | эгрес-1 20 | p | bus | 51 | 2222.5 | 111.125
1000003 | эгрэс-2 20 | p | bus | 60 | 398.88 | 19.944
1000004 | Таш.ГРЭС | p | bus | 224 | 456 | 22.8
1000005 | Оскаровка 220 | p | bus | 306 | -8.25 | 0.04
1000006 | Нура 220 | p | bus | 310 | -27.41 | 0.04
1000007 | Кар.ГРЭС-2 110 | p | bus | 356 | 300.05 | 15.0025
1000008 | Кумколь 110 | p | bus | 455 | 117.21 | 5.8605
1000009 | Агадырь 220 | p | bus | 468 | -73.41 | 0.04
1000010 | Балхашская 110 | p | bus | 472 | 105.62 | 5.281
1000011 | ПС 500 кВ Житикара - СШ 500 кВ | p | bus | 577 | -159 | 0.04
1000012 | Жамбыл 220 | p | bus | 801 | -217.01 | 0.04
1000013 | жгрэс-220 | p | bus | 805 | 226.01 | 11.3005
1000014 | Шымкент 220 | p | bus | 831 | -123.39 | 0.04
1000015 | Кентау | p | bus | 840 | -26.86 | 0.04
1000016 | Миргалимсай | p | bus | 842 | -17.29 | 0.04
1000017 | Шымкентская | p | bus | 843 | -182.21 | 0.04
1000018 | Кызылорда 220 | p | bus | 862 | -16.08 | 0.04
1000019 | Ру-6 | p | bus | 869 | -35.76 | 0.04
1000020 | ЮкГрэс 220 | p | bus | 901 | -19.28 | 0.04
1000021 | АТЭЦ-3 110 | p | bus | 905 | 150.48 | 7.524
1000022 | ПС-7 АХБК 110 | p | bus | 913 | 283.46 | 14.173
1000023 | Западная 220 | p | bus | 918 | -43.69 | 0.04
1000024 | Шу 220 | p | bus | 932 | -23.94 | 0.04
1000025 | Мойнакская ГЭС | p | bus | 935 | 129.81 | 6.4905
1000026 | еэк-20-бл5-8 | q | bus | 30 | -0.2 | 0.04
1000027 | эгрэс-1 бл3-2 | q | bus | 50 | 39.74 | 1.987
1000028 | эгрес-1 20 | q | bus | 51 | 123.31 | 6.1655
1000029 | эгрэс-2 20 | q | bus | 60 | 86.43 | 4.3215
1000030 | Таш.ГРЭС | q | bus | 224 | 204 | 10.2
1000031 | Оскаровка 220 | q | bus | 306 | -19.44 | 0.04
1000032 | Нура 220 | q | bus | 310 | -3.22 | 0.04
1000033 | Кар.ГРЭС-2 110 | q | bus | 356 | 1.89 | 0.0945
1000034 | Агадырь 220 | q | bus | 468 | 5.22 | 0.261
1000035 | Агадырь | q | bus | 469 | -40.74 | 0.04
1000036 | ПС 500 кВ Житикара - СШ 500 кВ | q | bus | 577 | 42.72 | 2.136
1000037 | Жамбыл 220 | q | bus | 801 | -103.72 | 0.04
1000038 | Шымкент 220 | q | bus | 831 | -36.44 | 0.04
1000039 | Кентау | q | bus | 840 | -15.13 | 0.04
1000040 | Миргалимсай | q | bus | 842 | -29.11 | 0.04
1000041 | Шымкентская | q | bus | 843 | -116.33 | 0.04
1000042 | Кызылорда 220 | q | bus | 862 | -13.52 | 0.04
1000043 | Ру-6 | q | bus | 869 | 0.81 | 0.0405
1000044 | ЮкГрэс 220 | q | bus | 901 | 0.52 | 0.04
1000045 | АТЭЦ-3 110 | q | bus | 905 | 61.16 | 3.058
1000046 | ПС-7 АХБК 110 | q | bus | 913 | 110.69 | 5.5345
1000047 | Шу 220 | q | bus | 932 | 11.88 | 0.594
1000048 | Алма | q | bus | 938 | -100.14 | 0.04
1000049 | Семей | q | bus | 980 | -132.13 | 0.04
1000050 | Талдыкорган | q | bus | 987 | -160.2 | 0.04
1000051 | ТАВРИЧЕСКАЯ | q | bus | 1817 | -16.51 | 0.04
1000057 | ЦГПП - ПС-ЦГПП 220 - ЦГПП АТ-4 | p | trafo | 6129130 | 260.71 | 13.0355 | 129
1000067 | ЖЕЗКАЗГАН - Жезказган 220 - Жезказган 500 АТ-1 | p | trafo | 16480466 | 146.92 | 7.346 | 480
1000088 | ЦГПП - ПС-ЦГПП 220 - ЦГПП АТ-4 | q | trafo | 6129130 | -70.36 | 0.04 | 129
1000098 | ЖЕЗКАЗГАН - Жезказган 220 - Жезказган 500 АТ-1 | q | trafo | 16480466 | 5.48 | 0.274 | 480
1000114 | ЭГРЭС-1 - ЭГРЭС-1 220 - ЭГРЭС-1 500 АТ | p | trafo | 12539 | -49.14 | 0.04 | 39
1000115 | ЭГРЭС-1 - эгрес-1 20 - ЭГРЭС-1 500 Т3-8 | p | trafo | 22551 | 2222.5 | 111.125 | 51
1000117 | ЕЭК - ПС-ЕЭК 220 - ЕЭК 500 АТ | p | trafo | 43133 | -402.91 | 0.04 | 33
1000118 | ЭГРЭС-1 220 - эгрэс-1 бл3-2 - эгрэс-1 Т1-2 | p | trafo | 53950 | 353.72 | 17.686 | 50
1000119 | ЦГПП - ПС-ЦГПП 220 - ЦГПП АТ-4 | p | trafo | 6129130 | -265.47 | 0.04 | 130
1000122 | Усть-Каменогорск - У-К - У-К 500 АТ-2 | p | trafo | 9240241 | 173.76 | 8.688 | 241
1000123 | Усть-Каменогорск - У-К - У-К 500 АТ-1 | p | trafo | 10240241 | 174.54 | 8.727 | 241
1000124 | Нура - Нура 220 - Нура 500 АТ-1 | p | trafo | 11325310 | -160.85 | 0.04 | 310
1000129 | ЖЕЗКАЗГАН - Жезказган 220 - Жезказган 500 АТ-1 | p | trafo | 16480466 | -146.3 | 0.04 | 466
1000130 | Жамбыл - Жамбыл 220 - Жамбыл АТ-1 | p | trafo | 17800801 | -150.9 | 0.04 | 801
1000131 | Шымкент - Шымкент 220 - Шымкент 500 АТ-1 | p | trafo | 18830831 | -133.61 | 0.04 | 831
1000132 | Шымкент - Шымкент 220 - Шымкент 500 АТ-3 | p | trafo | 19830831 | -108.69 | 0.04 | 831
1000133 | ЮКГРЭС - ЮкГрэс 220 - ЮКГРЭС АТ | p | trafo | 20900901 | -114.15 | 0.04 | 901
1000134 | Алматы - Алматы 220 - Алматы АТ-2 | p | trafo | 21902903 | -108.41 | 0.04 | 903
1000135 | Алматы - Алматы 220 - Алматы АТ-1 | p | trafo | 22902903 | -108.55 | 0.04 | 903
1000138 | Алма - Алма 220 - Алма АТ-2 | p | trafo | 25938939 | -196.75 | 0.04 | 939
1000139 | Алма - Алма 220 - Алма АТ-1 | p | trafo | 26938939 | -197.22 | 0.04 | 939
1000140 | Семей - Семей 220 - Семей 500 АТ-1 | p | trafo | 27980981 | 308.6 | 15.43 | 981
1000141 | Талдыкорган - Талдыкорган 220 - Талдыкорган 500 АТ-1 | p | trafo | 28987988 | -139.99 | 0.04 | 988
1000145 | ЭГРЭС-1 - ЭГРЭС-1 220 - ЭГРЭС-1 500 АТ | q | trafo | 12539 | 127.15 | 6.3575 | 39
1000146 | ЭГРЭС-1 - эгрес-1 20 - ЭГРЭС-1 500 Т3-8 | q | trafo | 22551 | 123.31 | 6.1655 | 51
1000147 | ЕЭК - еэк-20-бл5-8 - ЕЭК 500 Блок 5-8 | q | trafo | 33130 | -0.2 | 0.04 | 30
1000148 | ЕЭК - ПС-ЕЭК 220 - ЕЭК 500 АТ | q | trafo | 43133 | -310.16 | 0.04 | 33
1000149 | ЭГРЭС-1 220 - эгрэс-1 бл3-2 - эгрэс-1 Т1-2 | q | trafo | 53950 | 39.74 | 1.987 | 50
1000150 | ЦГПП - ПС-ЦГПП 220 - ЦГПП АТ-4 | q | trafo | 6129130 | -87.17 | 0.04 | 130
1000153 | Усть-Каменогорск - У-К - У-К 500 АТ-2 | q | trafo | 9240241 | -158.98 | 0.04 | 241
1000154 | Усть-Каменогорск - У-К - У-К 500 АТ-1 | q | trafo | 10240241 | -159.84 | 0.04 | 241
1000155 | Нура - Нура 220 - Нура 500 АТ-1 | q | trafo | 11325310 | 133.11 | 6.6555 | 310
1000160 | ЖЕЗКАЗГАН - Жезказган 220 - Жезказган 500 АТ-1 | q | trafo | 16480466 | -1.17 | 0.04 | 466
1000161 | Жамбыл - Жамбыл 220 - Жамбыл АТ-1 | q | trafo | 17800801 | 17.26 | 0.863 | 801
1000162 | Шымкент - Шымкент 220 - Шымкент 500 АТ-1 | q | trafo | 18830831 | -93 | 0.04 | 831
1000163 | Шымкент - Шымкент 220 - Шымкент 500 АТ-3 | q | trafo | 19830831 | -73.96 | 0.04 | 831
1000164 | ЮКГРЭС - ЮкГрэс 220 - ЮКГРЭС АТ | q | trafo | 20900901 | 52.71 | 2.6355 | 901
1000165 | Алматы - Алматы 220 - Алматы АТ-2 | q | trafo | 21902903 | 6.1 | 0.305 | 903
1000166 | Алматы - Алматы 220 - Алматы АТ-1 | q | trafo | 22902903 | -18.01 | 0.04 | 903
1000169 | Алма - Алма 220 - Алма АТ-2 | q | trafo | 25938939 | 88.14 | 4.407 | 939
1000170 | Алма - Алма 220 - Алма АТ-1 | q | trafo | 26938939 | 88.61 | 4.4305 | 939
1000171 | Семей - Семей 220 - Семей 500 АТ-1 | q | trafo | 27980981 | 19.62 | 0.981 | 981
1000172 | Талдыкорган - Талдыкорган 220 - Талдыкорган 500 АТ-1 | q | trafo | 28987988 | 29.47 | 1.4735 | 988
1000176 | ЭГРЭС-1 - ЕЭК - ВЛ5017 | p | line | 12531 | 296.83 | 14.8415 | 25
1000177 | ЭГРЭС-1 - ЦГПП - ВЛ5050 | p | line | 225129 | 325.69 | 16.2845 | 25
1000178 | ЭГРЭС-1 - Нура - ВЛ5120 | p | line | 325325 | 575.15 | 28.7575 | 25
1000179 | ЭГРЭС-1 - ТАВРИЧЕСКАЯ - ВЛ5577 | p | line | 4251817 | 284.63 | 14.2315 | 25
1000180 | ЭК-1150 - ЭГРЭС-1 - ВЛ5117 | p | line | 52625 | -320.37 | 0.04 | 26
1000181 | ЭК-1150 - ЭГРЭС-1 - ВЛ5107 | p | line | 62625 | -278.44 | 0.04 | 26
1000182 | ЭК-1150 - Кокшетау - ВЛ1101 | p | line | 726175 | 216.74 | 10.837 | 26
1000183 | ЭК-1150 - Агадырь - ВЛ5170 | p | line | 826469 | 578.23 | 28.9115 | 26
1000184 | ЭК-1150 - Алтай - ВЛ1104 | p | line | 9261660 | 66.91 | 3.3455 | 26
1000185 | ЭГРЕС-2 500 - ЭК-1150 - ВЛ5827 | p | line | 102826 | 180.13 | 9.0065 | 28
1000186 | ЭГРЕС-2 500 - ЭК-1150 - ВЛ5817 | p | line | 112826 | 193.98 | 9.699 | 28
1000188 | ЕЭК - Рубцовск - ВЛ5527 | p | line | 13311621 | 30.46 | 1.523 | 31
1000189 | ЕЭК - ИРТЫШСКАЯ - ВЛ5537 | p | line | 14311850 | 240.26 | 12.013 | 31
1000190 | ПС-ЕЭК 220 - пр/уз. ЕЭК Семей - ЭКВ | p | line | 15337202 | 7.95 | 0.3975 | 33
1000191 | ПС-ЕЭК 220 - пр/уз. Эгрэс-1 ЕЭК - ЭКВ | p | line | 16337203 | 63.27 | 3.1635 | 33
1000192 | ЭГРЭС-1 220 - пр/уз. Эгрэс-1 ЕЭК - ЭКВ | p | line | 17397203 | 43.72 | 2.186 | 39
1000193 | ЭГРЭС-1 220 - пр/уз.ЦГПП-ЭГРЭС-1 - ЭКВ | p | line | 18397204 | 72.24 | 3.612 | 39
1000194 | ЭГРЭС-1 220 - пр/уз.ЭГРЭС 1 Осакоровка - ЭКВ | p | line | 19397206 | 89.35 | 4.4675 | 39
1000195 | ЦГПП - ПС-ЕГПП - ВЛ5071 | p | line | 20129180 | 68.82 | 3.441 | 129
1000196 | ПС-ЦГПП 220 - пр/уз.ЦГПП-ЭГРЭС-1 - ЭКВ | p | line | 211307204 | -56.38 | 0.04 | 130
1000197 | ПС-ЦГПП 220 - пр/уз.ЦГПП-Осакоровка - ЭКВ | p | line | 221307205 | 64.95 | 3.2475 | 130
1000198 | АВРОРА 500 - ТАВРИЧЕСКАЯ - ВЛ5561 | p | line | 231471817 | -47.46 | 0.04 | 147
1000201 | Кокшетау - Костанай - ВЛ1102 | p | line | 26175590 | 15.03 | 0.7515 | 175
1000202 | ПС-ЕГПП - Сокол - ВЛ5086 | p | line | 27180576 | -3.16 | 0.04 | 180
1000203 | Таш.ГРЭС - Ташкент - ВЛ522 | p | line | 2822463 | 2934 | 146.7 | 224
1000204 | Таш.ГРЭС - Шымкент - ВЛ5019 | p | line | 29224830 | 471.1 | 23.555 | 224
1000205 | У-К - пр/уз. Семей У-К - ЭКВ | p | line | 302417201 | -148.62 | 0.04 | 241
1000206 | Оскаровка 220 - пр/уз.ЦГПП-Осакоровка - ЭКВ | p | line | 313067205 | -60.3 | 0.04 | 306
1000207 | Оскаровка 220 - пр/уз.ЭГРЭС 1 Осакоровка - ЭКВ | p | line | 323067206 | -60.39 | 0.04 | 306
1000208 | Оскаровка 220 - пр/уз.Кар.ГРЭС-2 Осакоровка - экв_ВЛ2258_ВЛ2268 | p | line | 333067229 | 98.8 | 4.94 | 306
1000209 | Нура 220 - пр/уз.КарГРЭС-Нура - ЭКВ | p | line | 343107208 | 129.13 | 6.4565 | 310
1000210 | Нура - Агадырь - ВЛ5138 | p | line | 35325469 | 419.22 | 20.961 | 325
1000211 | Кар.ГРЭС-2 - пр/уз.КарГРЭС-Нура - ЭКВ | p | line | 363557208 | -85.18 | 0.04 | 355
1000212 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Каражал - ЭКВ | p | line | 373557209 | 61.16 | 3.058 | 355
1000213 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Агадырь - ЭКВ | p | line | 383557210 | 56.76 | 2.838 | 355
1000214 | Кар.ГРЭС-2 - пр/уз.Каргрэс - Балхашская - ЭКВ | p | line | 393557211 | 56.23 | 2.8115 | 355
1000215 | Кар.ГРЭС-2 - пр/уз.Кар.ГРЭС-2 Осакоровка - экв_ВЛ2258_ВЛ2268 | p | line | 403557229 | -54.08 | 0.04 | 355
1000216 | Каражал 220 - Агадырь - ВЛ2428 | p | line | 41465468 | -33.24 | 0.04 | 465
1000217 | Каражал 220 - пр/уз.Каргрэс-Каражал - ЭКВ | p | line | 424657209 | -53.42 | 0.04 | 465
1000218 | Каражал 220 - пр/уз ЖезказганКаражал - ЭКВ | p | line | 434657221 | 79.66 | 3.983 | 465
1000219 | Жезказган 220 - Кумколь 220 - ЭКВ_2318_2328 | p | line | 44466467 | 49.25 | 2.4625 | 466
1000220 | Жезказган 220 - пр/уз ЖезказганКаражал - ЭКВ | p | line | 454667221 | 97.46 | 4.873 | 466
1000221 | Кумколь 220 - пр/уз Кызылорда-Кумколь - ЭКВ | p | line | 464677227 | 68.29 | 3.4145 | 467
1000223 | Агадырь 220 - пр/уз.Каргрэс-Агадырь - ЭКВ | p | line | 484687210 | -35.15 | 0.04 | 468
1000224 | Агадырь - ЖЕЗКАЗГАН - ВЛ5148 | p | line | 49469480 | 148.71 | 7.4355 | 469
1000225 | Агадырь - ЮКГРЭС - ВЛ5300 | p | line | 50469900 | 409.48 | 20.474 | 469
1000226 | Агадырь - ЮКГРЭС - ВЛ5320 | p | line | 51469900 | 413.44 | 20.672 | 469
1000227 | Балхашская - Мойынты - ВЛ2448 | p | line | 52473475 | -33.62 | 0.04 | 473
1000228 | Балхашская - пр/уз.Каргрэс - Балхашская - ЭКВ | p | line | 534737211 | -42.08 | 0.04 | 473
1000231 | Л-5726 (Сокол - Житикара) | p | line | 56576577 | 197.76 | 9.888 | 576
1000232 | Костанай - Сокол - ВЛ5096 | p | line | 57590576 | 396.31 | 19.8155 | 590
1000233 | Л-1103 (Костанайская - Челябинская) | p | line | 585904705 | -514.17 | 0.04 | 590
1000234 | Жамбыл - Шымкент - ВЛ5169 | p | line | 59800830 | -210.94 | 0.04 | 800
1000235 | Жамбыл 220 - жгрэс-220 - ЭКВ_Жамбыл_ЖГРЭС | p | line | 60801805 | -9.92 | 0.04 | 801
1000236 | Жамбыл 220 - пр/уз Жамбыл Шымкент - ЭКВ | p | line | 618017216 | -66.65 | 0.04 | 801
1000238 | Шымкент 220 - Шымкентская - ВЛ2349 | p | line | 63831843 | 49.42 | 2.471 | 831
1000239 | Шымкент 220 - пр/уз Жамбыл Шымкент - ЭКВ | p | line | 648317216 | 92.76 | 4.638 | 831
1000240 | Шымкент 220 - Пр/уз Шымкент-220/Жылга - ЭКВ | p | line | 658317225 | -23.15 | 0.04 | 831
1000241 | Шымкент 220 - ГНПС - ВЛ2309 | p | line | 668317228 | -4.52 | 0.04 | 831
1000245 | Кентау - Ру-6 - ВЛ2519 | p | line | 70840869 | 8.25 | 0.4125 | 840
1000246 | Кентау - пр/уз Кентау Жамбыл 220 - ЭКВ | p | line | 718407224 | -17.96 | 0.04 | 840
1000247 | Миргалимсай - Кентау - ВЛ2549 | p | line | 72842840 | 14.65 | 0.7325 | 842
1000248 | Миргалимсай - Шымкентская - ВЛ2319 | p | line | 73842843 | -38.24 | 0.04 | 842
1000249 | Кызылорда 220 - пр/уз Ру-6/Кызылорда - ЭКВ | p | line | 748627226 | 16.6 | 0.83 | 862
1000250 | Кызылорда 220 - пр/уз Кызылорда-Кумколь - ЭКВ | p | line | 758627227 | -35.29 | 0.04 | 862
1000251 | Жанакорган - Миргалимсай - ВЛ2539 | p | line | 76865842 | -8.4 | 0.04 | 865
1000252 | Жанакорган - Ру-6 - ВЛ2529 | p | line | 77865869 | 8.1 | 0.405 | 865
1000253 | Ру-6 - пр/уз Ру-6/Кызылорда - ЭКВ | p | line | 788697226 | -20.18 | 0.04 | 869
1000254 | ЮКГРЭС - Алматы - ВЛ5313 | p | line | 79900902 | 236.29 | 11.8145 | 900
1000255 | ЮКГРЭС - Алма - ВЛ5363 | p | line | 80900938 | 86.82 | 4.341 | 900
1000256 | ЮКГРЭС - ЧУ - ВЛ5333 | p | line | 819009932 | 348.66 | 17.433 | 900
1000257 | ЮкГрэс 220 - пр/уз ЮкГРЭС ШУ - ЭКВ | p | line | 829017212 | 81.97 | 4.0985 | 901
1000258 | ЮкГрэс 220 - пр/уз МойынтыЮкгрэс - ЭКВ | p | line | 839017219 | 11.14 | 0.557 | 901
1000260 | Алматы - ЧУ - ВЛ5343 | p | line | 859029932 | 22.79 | 1.1395 | 902
1000261 | Алматы 220 - АТЭЦ-3 - ВЛ2013 | p | line | 86903904 | 13.75 | 0.6875 | 903
1000262 | Алматы 220 - Робот - ВЛ2053 | p | line | 87903907 | -64.22 | 0.04 | 903
1000263 | Алматы 220 - Медео - ВЛ2773 | p | line | 88903928 | 12.88 | 0.644 | 903
1000264 | Алматы 220 - пр/уз Алматы Алма - ЭКВ | p | line | 899037213 | 117.82 | 5.891 | 903
1000265 | АТЭЦ-3 - Алма 220 - ВЛ2113 и ВЛ2103 | p | line | 90904939 | -278 | 0.04 | 904
1000266 | Робот - пр/уз ТалдыкорганРобот - ЭКВ | p | line | 919077218 | -92.9 | 0.04 | 907
1000267 | ПС-7 АХБК - Коян-Кос - ЭКВ | p | line | 92912953 | -176.22 | 0.04 | 912
1000268 | Западная 220 - ПС-7 АХБК - ВЛ2173 | p | line | 93918912 | -50.33 | 0.04 | 918
1000269 | Западная 220 - Кемин 220 - ВЛ2183 | p | line | 949182952 | 68.89 | 3.4445 | 918
1000271 | Шу 220 - Аспара - ВЛ2233 | p | line | 96932814 | -15.66 | 0.04 | 932
1000272 | Шу 220 - Главная 220 - ВЛ2163 | p | line | 979321916 | 84.58 | 4.229 | 932
1000273 | Шу 220 - пр/уз ЮкГРЭС ШУ - ЭКВ | p | line | 989327212 | -62.65 | 0.04 | 932
1000274 | Мойнакская ГЭС - Робот | p | line | 99935907 | 46.22 | 2.311 | 935
1000275 | Мойнакская ГЭС - Чилик | p | line | 100935911 | 83.58 | 4.179 | 935
1000276 | Алма 220 - Робот - ВЛ2463 | p | line | 101939907 | -55.99 | 0.04 | 939
1000278 | Алма 220 - пр/уз Алматы Алма - ЭКВ | p | line | 1039397213 | 217.59 | 10.8795 | 939
1000280 | Семей - ЭК-1150 - ВЛ5370 | p | line | 10598026 | -93.66 | 0.04 | 980
1000281 | Семей - Усть-Каменогорск - ВЛ5384 | p | line | 106980240 | -145.84 | 0.04 | 980
1000282 | Семей - Актогай - ВЛ5394 | p | line | 107980986 | 543.82 | 27.191 | 980
1000283 | Семей 220 - пр/уз. Семей У-К - ЭКВ | p | line | 1089817201 | -433.71 | 0.04 | 981
1000284 | Семей 220 - пр/уз. ЕЭК Семей - ЭКВ | p | line | 1099817202 | 9.57 | 0.4785 | 981
1000285 | Актогай - Талдыкорган - ВЛ5400 | p | line | 110986987 | 462.8 | 23.14 | 986
1000286 | Талдыкорган - Алма - ВЛ5413 | p | line | 111987938 | 310.06 | 15.503 | 987
1000287 | Талдыкорган 220 - пр/уз ТалдыкорганРобот - ЭКВ | p | line | 1129887218 | 94.56 | 4.728 | 988
1000288 | Рубцовск - Усть-Каменогорск - ВЛ5544 | p | line | 1131621240 | -202.28 | 0.04 | 1621
1000289 | Барнаул - Рубцовск - ВЛ551 | p | line | 11416301621 | 28.53 | 1.4265 | 1630
1000291 | Алтай - Барнаул - ВЛ596 | p | line | 11616601630 | -158.72 | 0.04 | 1660
1000292 | Алтай - Барнаул - ВЛ595 | p | line | 11716601630 | -110.96 | 0.04 | 1660
1000295 | ТАВРИЧЕСКАЯ - ИРТЫШСКАЯ - ВЛ555 | p | line | 12018171850 | 30.26 | 1.513 | 1817
1000299 | Главная 220 - Алматы 220 - ВЛ2193 | p | line | 1241916903 | -112.68 | 0.04 | 1916
1000300 | Главная 220 - пр/уз Главная Кемин - ЭКВ | p | line | 12519167214 | 0.1 | 0.04 | 1916
1000301 | Главная 220 - пр/уз ГлавнаяФрунзе - ЭКВ | p | line | 12619167217 | -70.2 | 0.04 | 1916
1000304 | Фрунзе - Жамбыл - ВЛ5159 | p | line | 1292919800 | -69.42 | 0.04 | 2919
1000305 | Фрунзе - ГЕНЕРАЦИЯ ЦА-1 - ЭКВ_509 | p | line | 13029192921 | 27.72 | 1.386 | 2919
1000306 | ТашкентТэс 220 - Шымкентская - ВЛ2419 | p | line | 1312925843 | 103.63 | 5.1815 | 2925
1000307 | Кемин 220 - пр/уз Главная Кемин - ЭКВ | p | line | 13229527214 | -41.63 | 0.04 | 2952
1000322 | ЧУ - Фрунзе - ВЛ5143 | p | line | 14799322919 | 371.78 | 18.589 | 9932
1000324 | ЭГРЭС-1 - ЕЭК - ВЛ5017 | q | line | 12531 | 13.48 | 0.674 | 25
1000325 | ЭГРЭС-1 - ЦГПП - ВЛ5050 | q | line | 225129 | -154.58 | 0.04 | 25
1000326 | ЭГРЭС-1 - Нура - ВЛ5120 | q | line | 325325 | -151.88 | 0.04 | 25
1000327 | ЭГРЭС-1 - ТАВРИЧЕСКАЯ - ВЛ5577 | q | line | 4251817 | -194.8 | 0.04 | 25
1000328 | ЭК-1150 - ЭГРЭС-1 - ВЛ5117 | q | line | 52625 | -0.79 | 0.04 | 26
1000329 | ЭК-1150 - ЭГРЭС-1 - ВЛ5107 | q | line | 62625 | -7.91 | 0.04 | 26
1000330 | ЭК-1150 - Кокшетау - ВЛ1101 | q | line | 726175 | -67.24 | 0.04 | 26
1000331 | ЭК-1150 - Агадырь - ВЛ5170 | q | line | 826469 | -179 | 0.04 | 26
1000332 | ЭК-1150 - Алтай - ВЛ1104 | q | line | 9261660 | -337.36 | 0.04 | 26
1000336 | ЕЭК - Рубцовск - ВЛ5527 | q | line | 13311621 | -223.34 | 0.04 | 31
1000337 | ЕЭК - ИРТЫШСКАЯ - ВЛ5537 | q | line | 14311850 | -120.98 | 0.04 | 31
1000338 | ПС-ЕЭК 220 - пр/уз. ЕЭК Семей - ЭКВ | q | line | 15337202 | -22.01 | 0.04 | 33
1000339 | ПС-ЕЭК 220 - пр/уз. Эгрэс-1 ЕЭК - ЭКВ | q | line | 16337203 | -30.16 | 0.04 | 33
1000340 | ЭГРЭС-1 220 - пр/уз. Эгрэс-1 ЕЭК - ЭКВ | q | line | 17397203 | 5.7 | 0.285 | 39
1000341 | ЭГРЭС-1 220 - пр/уз.ЦГПП-ЭГРЭС-1 - ЭКВ | q | line | 18397204 | -72.24 | 0.04 | 39
1000342 | ЭГРЭС-1 220 - пр/уз.ЭГРЭС 1 Осакоровка - ЭКВ | q | line | 19397206 | -43.72 | 0.04 | 39
1000343 | ЦГПП - ПС-ЕГПП - ВЛ5071 | q | line | 20129180 | 8.7 | 0.435 | 129
1000344 | ПС-ЦГПП 220 - пр/уз.ЦГПП-ЭГРЭС-1 - ЭКВ | q | line | 211307204 | 22.76 | 1.138 | 130
1000345 | ПС-ЦГПП 220 - пр/уз.ЦГПП-Осакоровка - ЭКВ | q | line | 221307205 | -59.1 | 0.04 | 130
1000346 | АВРОРА 500 - ТАВРИЧЕСКАЯ - ВЛ5561 | q | line | 231471817 | -134.48 | 0.04 | 147
1000349 | Кокшетау - Костанай - ВЛ1102 | q | line | 26175590 | -132.1 | 0.04 | 175
1000350 | ПС-ЕГПП - Сокол - ВЛ5086 | q | line | 27180576 | -19.78 | 0.04 | 180
1000351 | Таш.ГРЭС - Ташкент - ВЛ522 | q | line | 2822463 | 204 | 10.2 | 224
1000353 | У-К - пр/уз. Семей У-К - ЭКВ | q | line | 302417201 | 35.15 | 1.7575 | 241
1000354 | Оскаровка 220 - пр/уз.ЦГПП-Осакоровка - ЭКВ | q | line | 313067205 | -26.1 | 0.04 | 306
1000355 | Оскаровка 220 - пр/уз.ЭГРЭС 1 Осакоровка - ЭКВ | q | line | 323067206 | 10.57 | 0.5285 | 306
1000356 | Оскаровка 220 - пр/уз.Кар.ГРЭС-2 Осакоровка - экв_ВЛ2258_ВЛ2268 | q | line | 333067229 | 10.44 | 0.522 | 306
1000357 | Нура 220 - пр/уз.КарГРЭС-Нура - ЭКВ | q | line | 343107208 | 129.3 | 6.465 | 310
1000358 | Нура - Агадырь - ВЛ5138 | q | line | 35325469 | -105.6 | 0.04 | 325
1000359 | Кар.ГРЭС-2 - пр/уз.КарГРЭС-Нура - ЭКВ | q | line | 363557208 | 43.82 | 2.191 | 355
1000360 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Каражал - ЭКВ | q | line | 373557209 | -46.46 | 0.04 | 355
1000361 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Агадырь - ЭКВ | q | line | 383557210 | -46.42 | 0.04 | 355
1000362 | Кар.ГРЭС-2 - пр/уз.Каргрэс - Балхашская - ЭКВ | q | line | 393557211 | -39.47 | 0.04 | 355
1000363 | Кар.ГРЭС-2 - пр/уз.Кар.ГРЭС-2 Осакоровка - экв_ВЛ2258_ВЛ2268 | q | line | 403557229 | -28.07 | 0.04 | 355
1000367 | Жезказган 220 - Кумколь 220 - ЭКВ_2318_2328 | q | line | 44466467 | -41.77 | 0.04 | 466
1000368 | Жезказган 220 - пр/уз ЖезказганКаражал - ЭКВ | q | line | 454667221 | 42.81 | 2.1405 | 466
1000369 | Кумколь 220 - пр/уз Кызылорда-Кумколь - ЭКВ | q | line | 464677227 | -23.28 | 0.04 | 467
1000371 | Агадырь 220 - пр/уз.Каргрэс-Агадырь - ЭКВ | q | line | 484687210 | 32.89 | 1.6445 | 468
1000372 | Агадырь - ЖЕЗКАЗГАН - ВЛ5148 | q | line | 49469480 | -241.27 | 0.04 | 469
1000373 | Агадырь - ЮКГРЭС - ВЛ5300 | q | line | 50469900 | -213.58 | 0.04 | 469
1000374 | Агадырь - ЮКГРЭС - ВЛ5320 | q | line | 51469900 | -207.39 | 0.04 | 469
1000375 | Балхашская - Мойынты - ВЛ2448 | q | line | 52473475 | -51.69 | 0.04 | 473
1000376 | Балхашская - пр/уз.Каргрэс - Балхашская - ЭКВ | q | line | 534737211 | 18.17 | 0.9085 | 473
1000379 | Л-5726 (Сокол - Житикара) | q | line | 56576577 | -15.82 | 0.04 | 576
1000380 | Костанай - Сокол - ВЛ5096 | q | line | 57590576 | -113.91 | 0.04 | 590
1000381 | Л-1103 (Костанайская - Челябинская) | q | line | 585904705 | -95.72 | 0.04 | 590
1000382 | Жамбыл - Шымкент - ВЛ5169 | q | line | 59800830 | -11.38 | 0.04 | 800
1000383 | Жамбыл 220 - жгрэс-220 - ЭКВ_Жамбыл_ЖГРЭС | q | line | 60801805 | -27.32 | 0.04 | 801
1000384 | Жамбыл 220 - пр/уз Жамбыл Шымкент - ЭКВ | q | line | 618017216 | -26.45 | 0.04 | 801
1000386 | Шымкент 220 - Шымкентская - ВЛ2349 | q | line | 63831843 | 114.86 | 5.743 | 831
1000387 | Шымкент 220 - пр/уз Жамбыл Шымкент - ЭКВ | q | line | 648317216 | 6.61 | 0.3305 | 831
1000388 | Шымкент 220 - Пр/уз Шымкент-220/Жылга - ЭКВ | q | line | 658317225 | 12.0079 | 0.6004 | 831
1000389 | Шымкент 220 - ГНПС - ВЛ2309 | q | line | 668317228 | -6.61 | 0.04 | 831
1000393 | Кентау - Ру-6 - ВЛ2519 | q | line | 70840869 | -20.36 | 0.04 | 840
1000394 | Кентау - пр/уз Кентау Жамбыл 220 - ЭКВ | q | line | 718407224 | -9.08 | 0.04 | 840
1000395 | Миргалимсай - Кентау - ВЛ2549 | q | line | 72842840 | -16.35 | 0.04 | 842
1000396 | Миргалимсай - Шымкентская - ВЛ2319 | q | line | 73842843 | 5.53 | 0.2765 | 842
1000397 | Кызылорда 220 - пр/уз Ру-6/Кызылорда - ЭКВ | q | line | 748627226 | -29.97 | 0.04 | 862
1000398 | Кызылорда 220 - пр/уз Кызылорда-Кумколь - ЭКВ | q | line | 758627227 | -4.39 | 0.04 | 862
1000399 | Жанакорган - Миргалимсай - ВЛ2539 | q | line | 76865842 | 1.92 | 0.096 | 865
1000400 | Жанакорган - Ру-6 - ВЛ2529 | q | line | 77865869 | -7.07 | 0.04 | 865
1000401 | Ру-6 - пр/уз Ру-6/Кызылорда - ЭКВ | q | line | 788697226 | 8.86 | 0.443 | 869
1000402 | ЮКГРЭС - Алматы - ВЛ5313 | q | line | 79900902 | -163.64 | 0.04 | 900
1000403 | ЮКГРЭС - Алма - ВЛ5363 | q | line | 80900938 | -210.62 | 0.04 | 900
1000404 | ЮКГРЭС - ЧУ - ВЛ5333 | q | line | 819009932 | -65.3 | 0.04 | 900
1000405 | ЮкГрэс 220 - пр/уз ЮкГРЭС ШУ - ЭКВ | q | line | 829017212 | -21.23 | 0.04 | 901
1000406 | ЮкГрэс 220 - пр/уз МойынтыЮкгрэс - ЭКВ | q | line | 839017219 | -29.93 | 0.04 | 901
1000408 | Алматы - ЧУ - ВЛ5343 | q | line | 859029932 | -73.57 | 0.04 | 902
1000409 | Алматы 220 - АТЭЦ-3 - ВЛ2013 | q | line | 86903904 | 33.94 | 1.697 | 903
1000410 | Алматы 220 - Робот - ВЛ2053 | q | line | 87903907 | 9.22 | 0.461 | 903
1000411 | Алматы 220 - Медео - ВЛ2773 | q | line | 88903928 | 31.5 | 1.575 | 903
1000412 | Алматы 220 - пр/уз Алматы Алма - ЭКВ | q | line | 899037213 | -72.22 | 0.04 | 903
1000413 | АТЭЦ-3 - Алма 220 - ВЛ2113 и ВЛ2103 | q | line | 90904939 | -37.03 | 0.04 | 904
1000414 | Робот - пр/уз ТалдыкорганРобот - ЭКВ | q | line | 919077218 | -11 | 0.04 | 907
1000415 | ПС-7 АХБК - Коян-Кос - ЭКВ | q | line | 92912953 | -39.96 | 0.04 | 912
1000416 | Западная 220 - ПС-7 АХБК - ВЛ2173 | q | line | 93918912 | -50.33 | 0.04 | 918
1000417 | Западная 220 - Кемин 220 - ВЛ2183 | q | line | 949182952 | 28.58 | 1.429 | 918
1000419 | Шу 220 - Аспара - ВЛ2233 | q | line | 96932814 | -6.09 | 0.04 | 932
1000420 | Шу 220 - Главная 220 - ВЛ2163 | q | line | 979321916 | 36.02 | 1.801 | 932
1000421 | Шу 220 - пр/уз ЮкГРЭС ШУ - ЭКВ | q | line | 989327212 | -2.96 | 0.04 | 932
1000422 | Мойнакская ГЭС - Робот | q | line | 99935907 | -8.86 | 0.04 | 935
1000423 | Мойнакская ГЭС - Чилик | q | line | 100935911 | 11.3 | 0.565 | 935
1000424 | Алма 220 - Робот - ВЛ2463 | q | line | 101939907 | -52.92 | 0.04 | 939
1000426 | Алма 220 - пр/уз Алматы Алма - ЭКВ | q | line | 1039397213 | -138.76 | 0.04 | 939
1000428 | Семей - ЭК-1150 - ВЛ5370 | q | line | 10598026 | -216.88 | 0.04 | 980
1000429 | Семей - Усть-Каменогорск - ВЛ5384 | q | line | 106980240 | -50.09 | 0.04 | 980
1000430 | Семей - Актогай - ВЛ5394 | q | line | 107980986 | -201.17 | 0.04 | 980
1000431 | Семей 220 - пр/уз. Семей У-К - ЭКВ | q | line | 1089817201 | 7.48 | 0.374 | 981
1000432 | Семей 220 - пр/уз. ЕЭК Семей - ЭКВ | q | line | 1099817202 | -55.32 | 0.04 | 981
1000433 | Актогай - Талдыкорган - ВЛ5400 | q | line | 110986987 | -124.58 | 0.04 | 986
1000434 | Талдыкорган - Алма - ВЛ5413 | q | line | 111987938 | -197.39 | 0.04 | 987
1000435 | Талдыкорган 220 - пр/уз ТалдыкорганРобот - ЭКВ | q | line | 1129887218 | -45.44 | 0.04 | 988
1000436 | Рубцовск - Усть-Каменогорск - ВЛ5544 | q | line | 1131621240 | -57.24 | 0.04 | 1621
1000437 | Барнаул - Рубцовск - ВЛ551 | q | line | 11416301621 | -39.94 | 0.04 | 1630
1000439 | Алтай - Барнаул - ВЛ596 | q | line | 11616601630 | 103.77 | 5.1885 | 1660
1000440 | Алтай - Барнаул - ВЛ595 | q | line | 11716601630 | 60.23 | 3.0115 | 1660
1000443 | ТАВРИЧЕСКАЯ - ИРТЫШСКАЯ - ВЛ555 | q | line | 12018171850 | 37.88 | 1.894 | 1817
1000448 | Главная 220 - пр/уз Главная Кемин - ЭКВ | q | line | 12519167214 | 0.1 | 0.04 | 1916
1000449 | Главная 220 - пр/уз ГлавнаяФрунзе - ЭКВ | q | line | 12619167217 | 18.19 | 0.9095 | 1916
1000454 | ТашкентТэс 220 - Шымкентская - ВЛ2419 | q | line | 1312925843 | 45.72 | 2.286 | 2925
1000470 | ЧУ - Фрунзе - ВЛ5143 | q | line | 14799322919 | -40.48 | 0.04 | 9932
1000472 | ЭГРЭС-1 - ЕЭК - ВЛ5017 | p | line | 12531 | -296.95 | 0.04 | 31
1000473 | ЭГРЭС-1 - ЦГПП - ВЛ5050 | p | line | 225129 | -328.28 | 0.04 | 129
1000474 | ЭГРЭС-1 - Нура - ВЛ5120 | p | line | 325325 | -569 | 0.04 | 325
1000475 | ЭГРЭС-1 - ТАВРИЧЕСКАЯ - ВЛ5577 | p | line | 4251817 | -274.6 | 0.04 | 1817
1000476 | ЭК-1150 - ЭГРЭС-1 - ВЛ5117 | p | line | 52625 | 318.11 | 15.9055 | 25
1000477 | ЭК-1150 - ЭГРЭС-1 - ВЛ5107 | p | line | 62625 | 272.82 | 13.641 | 25
1000478 | ЭК-1150 - Кокшетау - ВЛ1101 | p | line | 726175 | -215.95 | 0.04 | 175
1000479 | ЭК-1150 - Агадырь - ВЛ5170 | p | line | 826469 | -552.26 | 0.04 | 469
1000480 | ЭК-1150 - Алтай - ВЛ1104 | p | line | 9261660 | -68.27 | 0.04 | 1660
1000481 | ЭГРЕС-2 500 - ЭК-1150 - ВЛ5827 | p | line | 102826 | -185.89 | 0.04 | 26
1000482 | ЭГРЕС-2 500 - ЭК-1150 - ВЛ5817 | p | line | 112826 | -193.8 | 0.04 | 26
1000484 | ЕЭК - Рубцовск - ВЛ5527 | p | line | 13311621 | 22.64 | 1.132 | 1621
1000485 | ЕЭК - ИРТЫШСКАЯ - ВЛ5537 | p | line | 14311850 | -237.36 | 0.04 | 1850
1000491 | ЦГПП - ПС-ЕГПП - ВЛ5071 | p | line | 20129180 | -75.15 | 0.04 | 180
1000494 | АВРОРА 500 - ТАВРИЧЕСКАЯ - ВЛ5561 | p | line | 231471817 | -47.74 | 0.04 | 1817
1000497 | Кокшетау - Костанай - ВЛ1102 | p | line | 26175590 | -16.61 | 0.04 | 590
1000498 | ПС-ЕГПП - Сокол - ВЛ5086 | p | line | 27180576 | -2.37 | 0.04 | 576
1000500 | Таш.ГРЭС - Шымкент - ВЛ5019 | p | line | 29224830 | -456.6 | 0.04 | 830
1000506 | Нура - Агадырь - ВЛ5138 | p | line | 35325469 | -417.12 | 0.04 | 469
1000515 | Жезказган 220 - Кумколь 220 - ЭКВ_2318_2328 | p | line | 44466467 | -48.34 | 0.04 | 467
1000520 | Агадырь - ЖЕЗКАЗГАН - ВЛ5148 | p | line | 49469480 | -145.55 | 0.04 | 480
1000521 | Агадырь - ЮКГРЭС - ВЛ5300 | p | line | 50469900 | -404.79 | 0.04 | 900
1000522 | Агадырь - ЮКГРЭС - ВЛ5320 | p | line | 51469900 | -404.79 | 0.04 | 900
1000525 | Мойынты - Агадырь 220 - ВЛ2438 | p | line | 54475468 | 45.94 | 2.297 | 468
1000528 | Костанай - Сокол - ВЛ5096 | p | line | 57590576 | -397.89 | 0.04 | 576
1000530 | Жамбыл - Шымкент - ВЛ5169 | p | line | 59800830 | 210.09 | 10.5045 | 830
1000531 | Жамбыл 220 - жгрэс-220 - ЭКВ_Жамбыл_ЖГРЭС | p | line | 60801805 | 11.11 | 0.5555 | 805
1000533 | Аспара - жгрэс-220 - ВЛ2249 | p | line | 62814805 | 15.66 | 0.783 | 805
1000534 | Шымкент 220 - Шымкентская - ВЛ2349 | p | line | 63831843 | -46.99 | 0.04 | 843
1000538 | Жылга - Шымкентская - ВЛ2449 | p | line | 67839843 | -66.83 | 0.04 | 843
1000539 | Жылга - ТашкентТэс 220 - ВЛ2429 | p | line | 688392925 | 100.58 | 5.029 | 2925
1000541 | Кентау - Ру-6 - ВЛ2519 | p | line | 70840869 | -8.68 | 0.04 | 869
1000543 | Миргалимсай - Кентау - ВЛ2549 | p | line | 72842840 | -17.33 | 0.04 | 840
1000544 | Миргалимсай - Шымкентская - ВЛ2319 | p | line | 73842843 | 40.93 | 2.0465 | 843
1000547 | Жанакорган - Миргалимсай - ВЛ2539 | p | line | 76865842 | 7.35 | 0.3675 | 842
1000548 | Жанакорган - Ру-6 - ВЛ2529 | p | line | 77865869 | -7.61 | 0.04 | 869
1000550 | ЮКГРЭС - Алматы - ВЛ5313 | p | line | 79900902 | -241.04 | 0.04 | 902
1000551 | ЮКГРЭС - Алма - ВЛ5363 | p | line | 80900938 | -93.57 | 0.04 | 938
1000552 | ЮКГРЭС - ЧУ - ВЛ5333 | p | line | 819009932 | -351.92 | 0.04 | 9932
1000556 | Алматы - ЧУ - ВЛ5343 | p | line | 859029932 | -31.77 | 0.04 | 9932
1000557 | Алматы 220 - АТЭЦ-3 - ВЛ2013 | p | line | 86903904 | -13.3 | 0.04 | 904
1000558 | Алматы 220 - Робот - ВЛ2053 | p | line | 87903907 | 65.7 | 3.285 | 907
1000561 | АТЭЦ-3 - Алма 220 - ВЛ2113 и ВЛ2103 | p | line | 90904939 | 278.25 | 13.9125 | 939
1000564 | Западная 220 - ПС-7 АХБК - ВЛ2173 | p | line | 93918912 | 112.57 | 5.6285 | 912
1000565 | Западная 220 - Кемин 220 - ВЛ2183 | p | line | 949182952 | -62.62 | 0.04 | 2952
1000566 | Медео - АТЭЦ-3 - ВЛ2023 | p | line | 95928904 | -5.68 | 0.04 | 904
1000568 | Шу 220 - Главная 220 - ВЛ2163 | p | line | 979321916 | -82.2 | 0.04 | 1916
1000570 | Мойнакская ГЭС - Робот | p | line | 99935907 | -45.2 | 0.04 | 907
1000572 | Алма 220 - Робот - ВЛ2463 | p | line | 101939907 | 55.7 | 2.785 | 907
1000575 | Коян-Кос - АТЭЦ-3 - ЭКВ | p | line | 104953904 | 184.72 | 9.236 | 904
1000576 | Семей - ЭК-1150 - ВЛ5370 | p | line | 10598026 | 96.0023 | 4.8001 | 26
1000577 | Семей - Усть-Каменогорск - ВЛ5384 | p | line | 106980240 | 142.84 | 7.142 | 240
1000578 | Семей - Актогай - ВЛ5394 | p | line | 107980986 | -535.76 | 0.04 | 986
1000581 | Актогай - Талдыкорган - ВЛ5400 | p | line | 110986987 | -460.14 | 0.04 | 987
1000582 | Талдыкорган - Алма - ВЛ5413 | p | line | 111987938 | -311.08 | 0.04 | 938
1000584 | Рубцовск - Усть-Каменогорск - ВЛ5544 | p | line | 1131621240 | 198.24 | 9.912 | 240
1000585 | Барнаул - Рубцовск - ВЛ551 | p | line | 11416301621 | 36.82 | 1.841 | 1621
1000587 | Алтай - Барнаул - ВЛ596 | p | line | 11616601630 | -155.97 | 0.04 | 1630
1000588 | Алтай - Барнаул - ВЛ595 | p | line | 11716601630 | 109.48 | 5.474 | 1630
1000591 | ТАВРИЧЕСКАЯ - ИРТЫШСКАЯ - ВЛ555 | p | line | 12018171850 | -27.51 | 0.04 | 1850
1000595 | Главная 220 - Алматы 220 - ВЛ2193 | p | line | 1241916903 | 112.07 | 5.6035 | 903
1000600 | Фрунзе - Жамбыл - ВЛ5159 | p | line | 1292919800 | 53.43 | 2.6715 | 800
1000602 | ТашкентТэс 220 - Шымкентская - ВЛ2419 | p | line | 1312925843 | -104.42 | 0.04 | 843
1000611 | Л-5736 (Ириклинская ГРЭС -Житикара) | p | line | 1404790577 | -81.48 | 0.04 | 577
1000613 | Л-5716 (Троицкая ГРЭС - Сокол) | p | line | 1424799576 | 88.6 | 4.43 | 576
1000614 | пр/уз жгрэс- Фрунзе - жгрэс-220 - ЭКВ | p | line | 1437223805 | 24.71 | 1.2355 | 805
1000615 | пр/уз жгрэс- Фрунзе - Фрунзе 220 - ЭКВ | p | line | 14472232918 | -15.14 | 0.04 | 2918
1000616 | пр/уз Кентау Жамбыл 220 - Жамбыл 220 - ЭКВ | p | line | 1457224801 | 26.45 | 1.3225 | 801
1000618 | ЧУ - Фрунзе - ВЛ5143 | p | line | 14799322919 | -374 | 0.04 | 2919
1000620 | ЭГРЭС-1 - ЕЭК - ВЛ5017 | q | line | 12531 | -126.05 | 0.04 | 31
1000621 | ЭГРЭС-1 - ЦГПП - ВЛ5050 | q | line | 225129 | 63.28 | 3.164 | 129
1000622 | ЭГРЭС-1 - Нура - ВЛ5120 | q | line | 325325 | -33.07 | 0.04 | 325
1000623 | ЭГРЭС-1 - ТАВРИЧЕСКАЯ - ВЛ5577 | q | line | 4251817 | -164.71 | 0.04 | 1817
1000624 | ЭК-1150 - ЭГРЭС-1 - ВЛ5117 | q | line | 52625 | -4.78 | 0.04 | 25
1000625 | ЭК-1150 - ЭГРЭС-1 - ВЛ5107 | q | line | 62625 | -5.06 | 0.04 | 25
1000626 | ЭК-1150 - Кокшетау - ВЛ1101 | q | line | 726175 | 140.01 | 7.0005 | 175
1000627 | ЭК-1150 - Агадырь - ВЛ5170 | q | line | 826469 | 42 | 2.1 | 469
1000628 | ЭК-1150 - Алтай - ВЛ1104 | q | line | 9261660 | -435.38 | 0.04 | 1660
1000629 | ЭГРЕС-2 500 - ЭК-1150 - ВЛ5827 | q | line | 102826 | 31.64 | 1.582 | 26
1000630 | ЭГРЕС-2 500 - ЭК-1150 - ВЛ5817 | q | line | 112826 | -27.69 | 0.04 | 26
1000632 | ЕЭК - Рубцовск - ВЛ5527 | q | line | 13311621 | 115.32 | 5.766 | 1621
1000633 | ЕЭК - ИРТЫШСКАЯ - ВЛ5537 | q | line | 14311850 | -73.17 | 0.04 | 1850
1000639 | ЦГПП - ПС-ЕГПП - ВЛ5071 | q | line | 20129180 | -56.16 | 0.04 | 180
1000642 | АВРОРА 500 - ТАВРИЧЕСКАЯ - ВЛ5561 | q | line | 231471817 | 149.71 | 7.4855 | 1817
1000645 | Кокшетау - Костанай - ВЛ1102 | q | line | 26175590 | -11.87 | 0.04 | 590
1000646 | ПС-ЕГПП - Сокол - ВЛ5086 | q | line | 27180576 | -94.92 | 0.04 | 576
1000648 | Таш.ГРЭС - Шымкент - ВЛ5019 | q | line | 29224830 | -29.38 | 0.04 | 830
1000654 | Нура - Агадырь - ВЛ5138 | q | line | 35325469 | -109.43 | 0.04 | 469
1000663 | Жезказган 220 - Кумколь 220 - ЭКВ_2318_2328 | q | line | 44466467 | -29.45 | 0.04 | 467
1000668 | Агадырь - ЖЕЗКАЗГАН - ВЛ5148 | q | line | 49469480 | -6.72 | 0.04 | 480
1000669 | Агадырь - ЮКГРЭС - ВЛ5300 | q | line | 50469900 | -103.24 | 0.04 | 900
1000670 | Агадырь - ЮКГРЭС - ВЛ5320 | q | line | 51469900 | -105.02 | 0.04 | 900
1000673 | Мойынты - Агадырь 220 - ВЛ2438 | q | line | 54475468 | -23.84 | 0.04 | 468
1000676 | Костанай - Сокол - ВЛ5096 | q | line | 57590576 | 78.31 | 3.9155 | 576
1000678 | Жамбыл - Шымкент - ВЛ5169 | q | line | 59800830 | -144.48 | 0.04 | 830
1000679 | Жамбыл 220 - жгрэс-220 - ЭКВ_Жамбыл_ЖГРЭС | q | line | 60801805 | 20.65 | 1.0325 | 805
1000681 | Аспара - жгрэс-220 - ВЛ2249 | q | line | 62814805 | -27.71 | 0.04 | 805
1000682 | Шымкент 220 - Шымкентская - ВЛ2349 | q | line | 63831843 | -114.23 | 0.04 | 843
1000689 | Кентау - Ру-6 - ВЛ2519 | q | line | 70840869 | -5.22 | 0.04 | 869
1000691 | Миргалимсай - Кентау - ВЛ2549 | q | line | 72842840 | 14.2 | 0.71 | 840
1000692 | Миргалимсай - Шымкентская - ВЛ2319 | q | line | 73842843 | -28.61 | 0.04 | 843
1000695 | Жанакорган - Миргалимсай - ВЛ2539 | q | line | 76865842 | -16.35 | 0.04 | 842
1000696 | Жанакорган - Ру-6 - ВЛ2529 | q | line | 77865869 | -2.57 | 0.04 | 869
1000698 | ЮКГРЭС - Алматы - ВЛ5313 | q | line | 79900902 | -107.66 | 0.04 | 902
1000699 | ЮКГРЭС - Алма - ВЛ5363 | q | line | 80900938 | -118.63 | 0.04 | 938
1000700 | ЮКГРЭС - ЧУ - ВЛ5333 | q | line | 819009932 | -114.92 | 0.04 | 9932
1000704 | Алматы - ЧУ - ВЛ5343 | q | line | 859029932 | -170.69 | 0.04 | 9932
1000705 | Алматы 220 - АТЭЦ-3 - ВЛ2013 | q | line | 86903904 | -43.82 | 0.04 | 904
1000706 | Алматы 220 - Робот - ВЛ2053 | q | line | 87903907 | -18.2 | 0.04 | 907
1000709 | АТЭЦ-3 - Алма 220 - ВЛ2113 и ВЛ2103 | q | line | 90904939 | 35.86 | 1.793 | 939
1000712 | Западная 220 - ПС-7 АХБК - ВЛ2173 | q | line | 93918912 | 5.03 | 0.2515 | 912
1000714 | Медео - АТЭЦ-3 - ВЛ2023 | q | line | 95928904 | -35.82 | 0.04 | 904
1000716 | Шу 220 - Главная 220 - ВЛ2163 | q | line | 979321916 | -48.67 | 0.04 | 1916
1000718 | Мойнакская ГЭС - Робот | q | line | 99935907 | -22.2 | 0.04 | 907
1000720 | Алма 220 - Робот - ВЛ2463 | q | line | 101939907 | 47.8 | 2.39 | 907
1000723 | Коян-Кос - АТЭЦ-3 - ЭКВ | q | line | 104953904 | 52.36 | 2.618 | 904
1000724 | Семей - ЭК-1150 - ВЛ5370 | q | line | 10598026 | -209.27 | 0.04 | 26
1000725 | Семей - Усть-Каменогорск - ВЛ5384 | q | line | 106980240 | -140.47 | 0.04 | 240
1000726 | Семей - Актогай - ВЛ5394 | q | line | 107980986 | -77.02 | 0.04 | 986
1000729 | Актогай - Талдыкорган - ВЛ5400 | q | line | 110986987 | -95.63 | 0.04 | 987
1000730 | Талдыкорган - Алма - ВЛ5413 | q | line | 111987938 | 16.71 | 0.8355 | 938
1000732 | Рубцовск - Усть-Каменогорск - ВЛ5544 | q | line | 1131621240 | -204.73 | 0.04 | 240
1000733 | Барнаул - Рубцовск - ВЛ551 | q | line | 11416301621 | 146 | 7.3 | 1621
1000735 | Алтай - Барнаул - ВЛ596 | q | line | 11616601630 | -107.26 | 0.04 | 1630
1000736 | Алтай - Барнаул - ВЛ595 | q | line | 11716601630 | 68.27 | 3.4135 | 1630
1000739 | ТАВРИЧЕСКАЯ - ИРТЫШСКАЯ - ВЛ555 | q | line | 12018171850 | 74.02 | 3.701 | 1850
1000743 | Главная 220 - Алматы 220 - ВЛ2193 | q | line | 1241916903 | 23.32 | 1.166 | 903
1000748 | Фрунзе - Жамбыл - ВЛ5159 | q | line | 1292919800 | -134.6 | 0.04 | 800
1000750 | ТашкентТэс 220 - Шымкентская - ВЛ2419 | q | line | 1312925843 | 25.9 | 1.295 | 843
1000759 | Л-5736 (Ириклинская ГРЭС -Житикара) | q | line | 1404790577 | -75.15 | 0.04 | 577
1000761 | Л-5716 (Троицкая ГРЭС - Сокол) | q | line | 1424799576 | -67.24 | 0.04 | 576
1000762 | пр/уз жгрэс- Фрунзе - жгрэс-220 - ЭКВ | q | line | 1437223805 | -6.11 | 0.04 | 805
1000764 | пр/уз Кентау Жамбыл 220 - Жамбыл 220 - ЭКВ | q | line | 1457224801 | -40.72 | 0.04 | 801

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
25 | 0.93581 | 31.8309 | 0 | 0 | 1.0301
26 | 0.93607 | 31.5024 | 0 | 0 | 1.0296
28 | 0.94391 | 32.868 | 0 | 0 | 1.0338
30 | 1 | 48.1416 | -797 | -353.9365 | 1
31 | 0.96524 | 32.4105 | 430 | 120 | 1.0165
33 | 1.0727 | 34.7613 | -597.2 | -373.354 | 1.0727
39 | 0.98508 | 31.001 | 360 | 50 | 1.0487
50 | 1 | 36.9379 | -476 | -544.0151 | 1
51 | 1 | 76.7637 | -2816 | -1597.2271 | 1
60 | 1 | 46.8582 | -939 | -534.973 | 1
129 | 1.0421 | 16.3918 | 0 | 0 | 1.0305
130 | 1.0818 | 12.7999 | 582 | -604.96 | 1.0818
147 | 1.01 | 21.1354 | -18 | -420.5873 | 1.0143
175 | 0.97043 | 17.9508 | 255 | 60 | 1.0238
180 | 1.0786 | 13.7729 | 103.5 | -99.4 | 1.0027
224 | 1.02 | -44.6793 | -434 | 339.6164 | 1.02
240 | 0.99 | 26.9212 | 0 | 0 | 1.0091
241 | 1.05 | 29.0297 | -461 | -225.9513 | 1.05
306 | 1.039 | 10.823 | 20.5 | 5.1 | 1.074
310 | 1.0001 | 5.4815 | 67 | 20 | 1.05
325 | 0.89162 | 10.1193 | 0 | 0 | 1.0221
355 | 1.0439 | 1.9518 | 0 | 0 | 1.0606
356 | 1.1 | 7.5448 | -183 | -107.606 | 1.1
455 | 1.1 | -23.8504 | -15.4 | -69.6925 | 1.1
465 | 0.97302 | -11.5761 | 33 | 3.2 | 1.0761
466 | 1.0682 | -14.9564 | -76 | -365.2237 | 1.1019
467 | 1.0443 | -24.4548 | 0 | 0 | 1.0753
468 | 0.93868 | -5.5566 | 0 | 0 | 1.0582
469 | 0.87095 | -5.3228 | 10 | 0 | 1.038
472 | 1.1 | -13.1604 | 79 | -67.7353 | 1.1
473 | 0.98783 | -8.8572 | 0 | 0 | 1.0605
475 | 0.95732 | -7.2709 | 6.4 | 2.1 | 1.0698
480 | 0.96967 | -12.482 | 0 | 0 | 1.0496
576 | 1 | 5.574 | 210 | -84.7072 | 1.0206
577 | 1.015 | 1.2495 | 256 | -33.8 | 1.0253
590 | 0.99395 | 6.9533 | 154 | 55 | 1.022
800 | 1.0268 | -46.8677 | 0 | 0 | 1.0252
801 | 1.0403 | -49.2059 | 265 | 20 | 1.0793
805 | 1.0545 | -48.1119 | -148 | -204.7034 | 1.0839
814 | 0.94664 | -41.3039 | 8 | 2 | 1.0743
830 | 1.0449 | -47.8121 | 0 | 0 | 1.0217
831 | 1.0773 | -50.5319 | 259.3 | -591.0376 | 1.0773
839 | 1.0536 | -52.0591 | 11.3 | 4.5 | 1.0609
840 | 1.0162 | -55.5444 | 20 | 4 | 1.0726
842 | 1.0149 | -55.7586 | 30 | 9.1 | 1.0691
843 | 1.0531 | -51.8154 | 195.3 | 45.3 | 1.0634
862 | 1 | -59.8936 | 101 | -56.3744 | 1
865 | 1.0025 | -57.961 | 18 | 3 | 1.0484
869 | 1.0003 | -58.6989 | 18 | 6 | 1.0338
900 | 0.92022 | -27.5032 | 0 | 0 | 1.042
901 | 0.91743 | -29.1156 | 3 | 2 | 1.0967
902 | 0.98633 | -34.392 | 0 | 0 | 1.0371
903 | 0.99272 | -37.0445 | 80 | 67.2 | 1.0701
904 | 1.0164 | -38.2971 | 0 | 0 | 1.0561
905 | 1.1 | -40.2221 | 38 | -38.573 | 1.1
907 | 1.0727 | -34.5039 | -121.3 | -310.5584 | 1.0818
911 | 1.063 | -35.7115 | 50 | 15 | 1.0891
912 | 1.0183 | -40.5572 | 0 | 0 | 1.0435
913 | 1.1 | -42.9445 | 91 | -63.1333 | 1.1
918 | 1.0106 | -46.3936 | 81.4 | 12.2 | 1.0316
928 | 1.0147 | -38.3027 | 40 | 12 | 1.0563
932 | 0.93995 | -40.7335 | 12 | 2 | 1.0723
935 | 1.1136 | -33.5109 | -78 | -76.9056 | 1.1136
938 | 1.0046 | -33.1632 | 0 | 0 | 1.042
939 | 1.0227 | -35.9798 | -15 | -548.4699 | 1.0651
953 | 1.0169 | -39.2877 | 12 | 2 | 1.0506
980 | 0.97712 | 20.6405 | 0 | 0 | 1.0181
981 | 1.0773 | 21.5349 | 170 | -689.116 | 1.0791
986 | 0.91364 | -6.4517 | 0 | 0 | 1.0142
987 | 0.99713 | -25.6465 | 0 | 0 | 1.038
988 | 1.0455 | -29.3525 | 166 | -426.2206 | 1.0902
1621 | 0.97817 | 28.2635 | 175 | 79 | 1.0097
1630 | 1.01 | 31.2639 | 165 | -225.4587 | 1.0146
1631 | 1 | 30.7928 | -185 | 2.4318 | 1.0258
1636 | 1.016 | 40.8201 | -353 | -28.1377 | 1.016
1660 | 1.0094 | 31.3425 | 0 | 0 | 1.0157
1817 | 0.95032 | 23.2233 | 385 | 114 | 1.0218
1850 | 0.94928 | 25.0829 | 174 | 11 | 1.0155
1852 | 0.97905 | 24.1062 | 1 | 1 | 1.0146
1853 | 0.95563 | 22.9696 | 178 | 40 | 1.02
1916 | 1.0045 | -58.6294 | 395 | -296.9645 | 0.96464
2918 | 0.9932 | -46.196 | 195 | 25 | 1.0108
2919 | 0.98953 | -42.4723 | 0 | 0 | 1.0264
2921 | 1.02 | -39.3552 | -225 | -101.837 | 1.02
2925 | 1.0455 | -44.7786 | -116 | -102.7253 | 1.0455
2952 | 1.0455 | -54.3062 | -30.3 | -191.5767 | 1.0455
4703 | 1 | 16.611 | -418 | 1.5633 | 1.0229
4705 | 1.005 | 9.6128 | 716 | -196 | 1.0333
4727 | 1 | 25.0244 | -680 | 4.6264 | 1.0192
4782 | 1 | 13.4483 | -439 | 192.4035 | 1.0254
4785 | 0.99743 | -0.094562 | 584.8 | 40 | 1.0282
4790 | 1.032 | 0 | 71.0924 | -217.5498 | 1.032
4799 | 1 | 7.1409 | 234 | 199.9053 | 0.99412
7201 | 1 | 25.9014 | -18 | 246.7942 | 1.0529
7202 | 1.0621 | 27.5001 | 24 | 9 | 1.0833
7203 | 1 | 31.4927 | 161 | 106.4613 | 1.0506
7204 | 1 | 21.4336 | 8 | 30.9147 | 1.0638
7205 | 1.0598 | 11.778 | 9.1 | 1.3 | 1.0815
7206 | 0.96344 | 18.6858 | 54 | 30.4 | 1.0345
7208 | 1.0591 | 1.6772 | 237.4 | -432.5056 | 1.0591
7209 | 0.99919 | -4.7814 | 7.4 | 2.4 | 1.0696
7210 | 0.98419 | -2.0113 | 20.3 | 7.9 | 1.0576
7211 | 1.0031 | -4.094 | 18 | 5.3 | 1.0712
7212 | 0.91912 | -35.5133 | 15 | 4.6 | 1.0852
7213 | 0.97748 | -39.3973 | 305 | 90 | 1.0565
7214 | 0.9978 | -61.0243 | 320 | 15 | 0.97975
7215 | 1.0168 | -50.3554 | 0 | 0 | 1.034
7216 | 1.0523 | -50.4624 | 55.1 | 16.2 | 1.0784
7217 | 0.97441 | -54.8467 | 175 | 30 | 0.96514
7218 | 1.055 | -32.4056 | 38.9 | 5 | 1.0893
7219 | 0.90788 | -30.1002 | 13 | 4.2 | 1.1004
7221 | 0.98829 | -16.7899 | 207 | 42.9 | 1.0735
7223 | 1.0216 | -47.4657 | 14 | 2 | 1.0502
7224 | 1.0173 | -53.5647 | 43 | 6.3 | 1.0791
7225 | 1.0594 | -51.869 | 29.9 | 7.7 | 1.0686
7226 | 1 | -59.3612 | 7 | -1.119 | 1.0194
7227 | 0.95131 | -48.3651 | 93 | -10 | 0.97511
7228 | 1.064 | -51.6444 | 20 | 3.4 | 1.0789
7229 | 1.0345 | 4.2241 | 24 | 19.3 | 1.0599
9917 | 0.97807 | 24.7513 | 146.3 | -42.2 | 1.034
9932 | 0.9698 | -37.9725 | 0 | 0 | 1.0308
10000 | 1.02 | 11.0432 | -550 | -472.8303 | 1.02

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent | Ppp | Prastr | Qpp | Qrastr
12531 | -77.421 | -181.2208 | 77.9618 | 187.6124 | 0.54076 | 6.3916 | 0.24316 | 0.24304 | 0.24316 | 0.93581 | 31.8309 | 0.96524 | 32.4105 | 0.11184 | 77.421 | 102.1757 | 181.2208 | -43.4848
225129 | 703.9552 | -236.4742 | -685.5692 | 462.2609 | 18.386 | 225.7867 | 0.91631 | 0.91618 | 0.91631 | 0.93581 | 31.8309 | 1.0421 | 16.3918 | 0.12298 | -703.9552 | -653.2797 | 236.4742 | 122.5359
325325 | 1008.2397 | 214.0317 | -967.9631 | 165.7071 | 40.2765 | 379.7388 | 1.2718 | 1.2718 | 1.2718 | 0.93581 | 31.8309 | 0.89162 | 10.1193 | 0.11218 | -1008.2397 | -1009.0997 | -214.0317 | 67.3387
4251817 | 303.0351 | -41.435 | -297.9939 | 87.3402 | 5.0412 | 45.9052 | 0.3774 | 0.37731 | 0.3774 | 0.93581 | 31.8309 | 0.95032 | 23.2233 | 0.085636 | -303.0351 | -347.2406 | 41.435 | 184.317
62625 | -394.4859 | 51.9816 | 394.6666 | -49.7137 | 0.18068 | 2.2679 | 0.49083 | 0.49083 | 0.49083 | 0.93607 | 31.5024 | 0.93581 | 31.8309 | 0.10168 | 394.4859 | 355.7438 | -51.9816 | 8.1723
52625 | -326.0117 | 43.6162 | 326.1648 | -41.7451 | 0.1531 | 1.8711 | 0.40574 | 0.40574 | 0.40574 | 0.93607 | 31.5024 | 0.93581 | 31.8309 | 0.10167 | 326.0117 | 430.3441 | -43.6162 | 8.2915
726175 | 399.5918 | -31.4019 | -395.1551 | 128.219 | 4.4367 | 96.8171 | 0.49444 | 0.49432 | 0.49444 | 0.93607 | 31.5024 | 0.97043 | 17.9508 | 0.081191 | -399.5918 | -486.5922 | 31.4019 | 240.9824
826469 | 910.8262 | 327.6646 | -861.2034 | 263.5992 | 49.6227 | 591.2638 | 1.194 | 1.1941 | 1.1941 | 0.93607 | 31.5024 | 0.87095 | -5.3228 | 0.11221 | -910.8262 | -944.7787 | -327.6646 | 87.75
9261660 | -2.5133 | -80.9727 | 2.953 | 86.6058 | 0.43968 | 5.6332 | 0.099932 | 0.099128 | 0.099932 | 0.93607 | 31.5024 | 1.0094 | 31.3425 | 0.022708 | 2.5133 | 11.8602 | 80.9727 | 362.0922
102826 | 457.058 | 131.2749 | -456.2357 | -119.3688 | 0.82234 | 11.9062 | 0.58173 | 0.58174 | 0.58174 | 0.94391 | 32.868 | 0.93607 | 31.5024 | 0.11175 | -457.058 | -459.5197 | -131.2749 | -51.7355
112826 | 477.8408 | 130.2855 | -476.8166 | -117.8955 | 1.0242 | 12.39 | 0.60589 | 0.60589 | 0.60589 | 0.94391 | 32.868 | 0.93607 | 31.5024 | 0.11184 | -477.8408 | -479.4803 | -130.2855 | -48.7104
12311621 | 168.8237 | -43.1233 | -167.4883 | 55.6525 | 1.3355 | 12.5292 | 0.20844 | 0.20834 | 0.20844 | 0.96524 | 32.4105 | 0.97817 | 28.2635 | 0.08433 | -168.8237 | -142.5615 | 43.1233 | 160.07
13311850 | 384.0325 | 36.2934 | -379.1644 | 12.5528 | 4.8681 | 48.8463 | 0.46146 | 0.46147 | 0.46147 | 0.96524 | 32.4105 | 0.94928 | 25.0829 | 0.09243 | -384.0325 | -418.2038 | -36.2934 | 135.1259
14337202 | 133.4082 | 6.4079 | -131.8259 | 10.3661 | 1.5822 | 16.774 | 0.32675 | 0.32674 | 0.32675 | 1.0727 | 34.7613 | 1.0621 | 27.5001 | 0.11185 | -133.4082 | -114.8794 | -6.4079 | 32.5678
15337203 | 195.3181 | 159.5164 | -190.2595 | -138.1057 | 5.0586 | 21.4107 | 0.61693 | 0.61698 | 0.61698 | 1.0727 | 34.7613 | 1 | 31.4927 | 0.1334 | -195.3181 | -186.133 | -159.5164 | -7.7358
16397203 | -29.0894 | -30.9497 | 29.2595 | 31.6444 | 0.17009 | 0.69468 | 0.11315 | 0.1131 | 0.11315 | 0.98508 | 31.001 | 1 | 31.4927 | 0.16885 | 29.0894 | 22.2938 | 30.9497 | 14.2504
17397204 | 124.2617 | -28.7283 | -119.5448 | 49.6933 | 4.7169 | 20.965 | 0.33977 | 0.33975 | 0.33977 | 0.98508 | 31.001 | 1 | 21.4336 | 0.10314 | -124.2617 | -122.624 | 28.7283 | 47.8782
18397206 | 141.675 | -5.4963 | -134.2298 | 34.786 | 7.4452 | 29.2897 | 0.37772 | 0.37771 | 0.37772 | 0.98508 | 31.001 | 0.96344 | 18.6858 | 0.10801 | -141.675 | -137.814 | 5.4963 | 23.1594
19129180 | 104.2888 | -91.7601 | -103.5 | 99.4 | 0.78885 | 7.6399 | 0.15392 | 0.15362 | 0.15392 | 1.0421 | 16.3918 | 1.0786 | 13.7729 | 0.053212 | -104.2888 | -104.0813 | 91.7601 | 134.4992
201307204 | -106.2157 | 104.2949 | 111.5448 | -80.608 | 5.3291 | 23.6868 | 0.36111 | 0.36116 | 0.36116 | 1.0818 | 12.7999 | 1 | 21.4336 | 0.12063 | 106.2157 | 107.2339 | -104.2949 | -28.9769
211307205 | 104.4303 | 74.625 | -103.5969 | -71.3084 | 0.83341 | 3.3165 | 0.31136 | 0.31142 | 0.31142 | 1.0818 | 12.7999 | 1.0598 | 11.778 | 0.18354 | -104.4303 | -62.2776 | -74.625 | 31.836
221471817 | -75.6328 | 183.2265 | 77.4023 | -169.9443 | 1.7695 | 13.2822 | 0.22662 | 0.2269 | 0.2269 | 1.01 | 21.1354 | 0.95032 | 23.2233 | 0.10234 | 75.6328 | 135.7654 | -183.2265 | 139.6293
231474727 | -197.0697 | 58.7657 | 198.624 | -45.0683 | 1.5543 | 13.6974 | 0.23511 | 0.23518 | 0.23518 | 1.01 | 21.1354 | 1 | 25.0244 | 0.098881 | 197.0697 | 164.3257 | -58.7657 | 121.2288
24175147 | -288.4197 | -155.9635 | 290.7025 | 178.5951 | 2.2828 | 22.6316 | 0.39015 | 0.39006 | 0.39015 | 0.97043 | 17.9508 | 1.01 | 21.1354 | 0.097561 | 288.4197 | 316.0282 | 155.9635 | -10.476
25175590 | 428.5748 | -32.2555 | -424.6365 | 115.7465 | 3.9383 | 83.491 | 0.5114 | 0.51131 | 0.5114 | 0.97043 | 17.9508 | 0.99395 | 6.9533 | 0.078951 | -428.5748 | -542.1603 | 32.2555 | 189.5116
26180576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0786 | 13.7729 | 1 | 5.574 | 0 | 0 | 0 | 0 | 0
2722463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1.02 | -44.6793 |  |  |  | 0 | 0 | 0 | 0
28224830 | 427.4926 | -222.9216 | -424.8119 | 251.8413 | 2.6807 | 28.9197 | 0.54579 | 0.54573 | 0.54579 | 1.02 | -44.6793 | 1.0449 | -47.8121 | 0.12975 | -427.4926 | -358.6374 | 222.9216 | 97.1823
292417201 | 125.907 | 91.849 | -124.5072 | -80.8309 | 1.3998 | 11.0181 | 0.38952 | 0.38956 | 0.38956 | 1.05 | 29.0297 | 1 | 25.9014 | 0.12381 | -125.907 | -121.2192 | -91.849 | 33.9699
303067205 | -93.7692 | -67.1118 | 94.4969 | 70.0084 | 0.72772 | 2.8967 | 0.29126 | 0.29121 | 0.29126 | 1.039 | 10.823 | 1.0598 | 11.778 | 0.18228 | 93.7692 | 52.8078 | 67.1118 | 38.5659
313067206 | -76.0927 | 81.4513 | 80.2298 | -65.186 | 4.1371 | 16.2654 | 0.28154 | 0.28158 | 0.28158 | 1.039 | 10.823 | 0.96344 | 18.6858 | 0.11673 | 76.0927 | 74.9063 | -81.4513 | -41.7341
323067229 | 149.3619 | -19.4395 | -145.5061 | 36.3048 | 3.8558 | 16.8653 | 0.38044 | 0.38044 | 0.38044 | 1.039 | 10.823 | 1.0345 | 4.2241 | 0.14479 | -149.3619 | -107.2139 | 19.4395 | 8.268
333107208 | 241.2024 | -321.9205 | -232.2449 | 357.0849 | 8.9575 | 35.1643 | 1.0555 | 1.0555 | 1.0555 | 1.0001 | 5.4815 | 1.0591 | 1.6772 | 0.17101 | -241.2024 | -224.7964 | 321.9205 | 102.2603
34325469 | 658.7643 | 89.2878 | -643.5096 | 87.0809 | 15.2547 | 176.3687 | 0.86093 | 0.86094 | 0.86094 | 0.89162 | 10.1193 | 0.87095 | -5.3228 | 0.10856 | -658.7643 | -681.1073 | -89.2878 | 169.9095
353557208 | 5.4373 | -74.3276 | -5.1551 | 75.4208 | 0.28217 | 1.0932 | 0.18736 | 0.18732 | 0.18736 | 1.0439 | 1.9518 | 1.0591 | 1.6772 | 0.45823 | -5.4373 | -11.7291 | 74.3276 | 3.0077
363557209 | 119.751 | 20.7861 | -116.1658 | -6.3351 | 3.5852 | 14.451 | 0.30555 | 0.30556 | 0.30556 | 1.0439 | 1.9518 | 0.99919 | -4.7814 | 0.11123 | -119.751 | -104.4833 | -20.7861 | 37.5231
373557210 | 108.5227 | 59.0128 | -105.9172 | -48.4445 | 2.6055 | 10.5683 | 0.31055 | 0.31056 | 0.31056 | 1.0439 | 1.9518 | 0.98419 | -2.0113 | 0.13882 | -108.5227 | -87.9493 | -59.0128 | 20.9686
383557211 | 68.6215 | 11.7095 | -66.758 | -4.2689 | 1.8635 | 7.4406 | 0.17501 | 0.17501 | 0.17501 | 1.0439 | 1.9518 | 1.0031 | -4.094 | 0.10446 | -68.6215 | -59.6022 | -11.7095 | 32.1291
393557229 | -120.2893 | 60.9224 | 121.5061 | -55.6048 | 1.2169 | 5.3175 | 0.33898 | 0.33898 | 0.33898 | 1.0439 | 1.9518 | 1.0345 | 4.2241 | 0.1622 | 120.2893 | 80.9293 | -60.9224 | -19.2168
40465468 | -55.7558 | 38.6624 | 57.4036 | -31.4706 | 1.6478 | 7.1917 | 0.18299 | 0.18302 | 0.18302 | 0.97302 | -11.5761 | 0.93868 | -5.5566 | 0.10146 | 55.7558 | 61.762 | -38.6624 | -17.814
414657209 | -105.628 | 8.7116 | 108.7658 | 3.9351 | 3.1378 | 12.6468 | 0.28585 | 0.28585 | 0.28585 | 0.97302 | -11.5761 | 0.99919 | -4.7814 | 0.11627 | 105.628 | 92.1041 | -8.7116 | -25.3106
424657221 | 128.3838 | -50.574 | -125.193 | 62.9645 | 3.1908 | 12.3905 | 0.37216 | 0.37211 | 0.37216 | 0.97302 | -11.5761 | 0.98829 | -16.7899 | 0.11795 | -128.3838 | -120.8172 | 50.574 | 46.3122
43466467 | 181.2885 | -2.6416 | -174.3802 | 31.7269 | 6.9084 | 29.0853 | 0.44544 | 0.44542 | 0.44544 | 1.0682 | -14.9564 | 1.0443 | -24.4548 | 0.10687 | -181.2885 | -171.2739 | 2.6416 | 35.9621
444667221 | 84.7142 | 117.1465 | -81.807 | -105.8645 | 2.9073 | 11.282 | 0.35518 | 0.35527 | 0.35527 | 1.0682 | -14.9564 | 0.98829 | -16.7899 | 0.14437 | -84.7142 | -89.0339 | -117.1465 | -4.1877
454677227 | 189.6213 | 33.7223 | -170.3747 | 41.8973 | 19.2465 | 75.6196 | 0.48401 | 0.48401 | 0.48401 | 1.0443 | -24.4548 | 0.95131 | -48.3651 | 0.10893 | -189.6213 | -181.161 | -33.7223 | -14.8105
46468473 | 19.671 | -26.3373 | -19.0716 | 28.8326 | 0.59937 | 2.4953 | 0.091903 | 0.091839 | 0.091903 | 0.93868 | -5.5566 | 0.98783 | -8.8572 | 0.11106 | -19.671 | -23.618 | 26.3373 | 23.5728
474687210 | -83.8933 | -33.5561 | 85.6172 | 40.5445 | 1.7238 | 6.9884 | 0.25261 | 0.2526 | 0.25261 | 0.93868 | -5.5566 | 0.98419 | -2.0113 | 0.14586 | 83.8933 | 65.5625 | 33.5561 | -12.3795
48469480 | 195.3476 | -181.5255 | -190.6263 | 227.2884 | 4.7213 | 45.7629 | 0.35355 | 0.35325 | 0.35355 | 0.87095 | -5.3228 | 0.96967 | -12.482 | 0.10396 | -195.3476 | -186.5321 | 181.5255 | 242.2039
50469900 | 636.1893 | -27.3076 | -611.6007 | 280.194 | 24.5886 | 252.8864 | 0.84423 | 0.84414 | 0.84423 | 0.87095 | -5.3228 | 0.92022 | -27.5032 | 0.11147 | -636.1893 | -674.2982 | 27.3076 | 189.8015
49469900 | 650.402 | -36.1411 | -621.9858 | 294.4901 | 28.4163 | 258.349 | 0.86363 | 0.86353 | 0.86363 | 0.87095 | -5.3228 | 0.92022 | -27.5032 | 0.11083 | -650.402 | -658.9096 | 36.1411 | 171.2337
51473475 | -12.44 | 23.955 | 12.6941 | -22.8927 | 0.2541 | 1.0623 | 0.07171 | 0.071759 | 0.071759 | 0.98783 | -8.8572 | 0.95732 | -7.2709 | 0.13159 | 12.44 | 16.144 | -23.955 | 15.0012
524737211 | -47.7676 | 4.9754 | 48.758 | -1.0311 | 0.99046 | 3.9443 | 0.12759 | 0.12759 | 0.12759 | 0.98783 | -8.8572 | 1.0031 | -4.094 | 0.12069 | 47.7676 | 39.5606 | -4.9754 | 9.2345
53475468 | -19.0941 | 20.7927 | 19.3241 | -19.8337 | 0.23006 | 0.95895 | 0.077387 | 0.077418 | 0.077418 | 0.95732 | -7.2709 | 0.93868 | -5.5566 | 0.091296 | 19.0941 | 22.6251 | -20.7927 | -7.0837
544757219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95732 | -7.2709 | 0.90788 | -30.1002 | 0 | 0 | 0 | 0 | 0
55576577 | 349.9788 | -87.5265 | -347.5323 | 115.2051 | 2.4465 | 27.6786 | 0.41657 | 0.41651 | 0.41657 | 1 | 5.574 | 1.015 | 1.2495 | 0.073719 | -349.9788 | -482.9138 | 87.5265 | 127.4349
56590576 | 425.8209 | -146.0172 | -424.7543 | 157.1359 | 1.0666 | 11.1187 | 0.52297 | 0.52295 | 0.52297 | 0.99395 | 6.9533 | 1 | 5.574 | 0.08103 | -425.8209 | -569.7917 | 146.0172 | 40.3751
575904705 | -155.1844 | -24.7293 | 155.5842 | 31.9007 | 0.39979 | 7.1713 | 0.18256 | 0.18248 | 0.18256 | 0.99395 | 6.9533 | 1.005 | 9.6128 | 0.05761 | 155.1844 | 187.2918 | 24.7293 | 208.7636
58800830 | 78.0631 | -95.9197 | -77.8254 | 98.7468 | 0.23768 | 2.8271 | 0.13908 | 0.13894 | 0.13908 | 1.0268 | -46.8677 | 1.0449 | -47.8121 | 0.10759 | -78.0631 | -68.4377 | 95.9197 | 67.6198
59801805 | -196.4556 | -74.152 | 197.6745 | 78.9388 | 1.2189 | 4.7868 | 0.52972 | 0.5297 | 0.52972 | 1.0403 | -49.2059 | 1.0545 | -48.1119 | 0.10367 | 196.4556 | 209.1763 | 74.152 | -3.6909
608017216 | 44.3825 | -38.8124 | -44.0245 | 40.207 | 0.35795 | 1.3946 | 0.14873 | 0.14869 | 0.14873 | 1.0403 | -49.2059 | 1.0523 | -50.4624 | 0.10341 | -44.3825 | -53.0555 | 38.8124 | 26.1572
61814805 | 49.6129 | -65.8993 | -46.1781 | 79.4163 | 3.4348 | 13.517 | 0.22868 | 0.22862 | 0.22868 | 0.94664 | -41.3039 | 1.0545 | -48.1119 | 0.12525 | -49.6129 | -66.214 | 65.8993 | 34.6723
62831843 | 130.0624 | 97.8428 | -129.2513 | -92.7772 | 0.81117 | 5.0656 | 0.39649 | 0.39649 | 0.39649 | 1.0773 | -50.5319 | 1.0531 | -51.8154 | 0.14552 | -130.0624 | -97.803 | -97.8428 | -50.05
638317216 | 11.408 | 57.6991 | -11.0755 | -56.407 | 0.33246 | 1.2921 | 0.14328 | 0.14335 | 0.14335 | 1.0773 | -50.5319 | 1.0523 | -50.4624 | 0.30941 | -11.408 | -2.326 | -57.6991 | 18.8762
648317225 | 36.2012 | 14.7647 | -35.9296 | -13.6993 | 0.27162 | 1.0655 | 0.095242 | 0.095255 | 0.095255 | 1.0773 | -50.5319 | 1.0594 | -51.869 | 0.21504 | -36.2012 | -2.1361 | -14.7647 | -3.5177
658317228 | 64.7999 | 23.8582 | -64.4476 | -22.3235 | 0.35231 | 1.5346 | 0.16822 | 0.16822 | 0.16822 | 1.0773 | -50.5319 | 1.064 | -51.6444 | 0.10247 | -64.7999 | -63.8534 | -23.8582 | 21.5352
66839843 | -5.2837 | 1.4604 | 5.2874 | -1.4522 | 0.0036663 | 0.0081747 | 0.013654 | 0.013664 | 0.013664 | 1.0536 | -52.0591 | 1.0531 | -51.8154 | 0.0099671 | 5.2837 | -52.4521 | -1.4604 | 17.9044
678392925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0536 | -52.0591 | 1.0455 | -44.7786 | 0 | 0 | 0 | 0 | 0
688397225 | -6.0163 | -5.9604 | 6.0296 | 5.9993 | 0.013308 | 0.038856 | 0.021095 | 0.02107 | 0.021095 | 1.0536 | -52.0591 | 1.0594 | -51.869 | 0.023256 | 6.0163 | -27.9796 | 5.9604 | 23.7042
69840869 | 32.014 | 1.7858 | -31.5621 | -0.048759 | 0.4519 | 1.7371 | 0.082801 | 0.082803 | 0.082803 | 1.0162 | -55.5444 | 1.0003 | -58.6989 | 0.07405 | -32.014 | -34.6887 | -1.7858 | 0.42318
708407224 | -31.1226 | 7.5474 | 31.3974 | -6.4988 | 0.27476 | 1.0486 | 0.0827 | 0.082714 | 0.082714 | 1.0162 | -55.5444 | 1.0173 | -53.5647 | 0.086801 | 31.1226 | 35.525 | -7.5474 | 10.3208
71842840 | -22.6704 | -1.755 | 22.6928 | 1.8394 | 0.022399 | 0.084408 | 0.058794 | 0.058794 | 0.058794 | 1.0149 | -55.7586 | 1.0162 | -55.5444 | 0.082073 | 22.6704 | 23.643 | 1.755 | 17.1076
72842843 | -47.4176 | -10.3116 | 48.348 | 14.032 | 0.93035 | 3.7204 | 0.12547 | 0.12546 | 0.12547 | 1.0149 | -55.7586 | 1.0531 | -51.8154 | 0.088338 | 47.4176 | 49.7605 | 10.3116 | -5.0633
738627226 | -28.0038 | 7.2992 | 28.0705 | -7.0592 | 0.066717 | 0.24002 | 0.075946 | 0.07596 | 0.07596 | 1 | -59.8936 | 1 | -59.3612 | 0.040201 | 28.0038 | 32.8138 | -7.2992 | 64.087
748627227 | -72.9962 | 49.0752 | 77.3747 | -31.8973 | 4.3785 | 17.1779 | 0.23083 | 0.23088 | 0.23088 | 1 | -59.8936 | 0.95131 | -48.3651 | 0.10541 | 72.9962 | 68.1952 | -49.0752 | -17.9861
75865842 | -39.6819 | -1.4219 | 40.088 | 2.9666 | 0.40611 | 1.5446 | 0.10394 | 0.10394 | 0.10394 | 1.0025 | -57.961 | 1.0149 | -55.7586 | 0.088882 | 39.6819 | 42.9459 | 1.4219 | 18.387
76865869 | 21.6819 | -1.5781 | -21.6118 | 1.8441 | 0.070043 | 0.266 | 0.056906 | 0.056904 | 0.056906 | 1.0025 | -57.961 | 1.0003 | -58.6989 | 0.06526 | -21.6819 | -24.3695 | 1.5781 | -15.1263
778697226 | 35.1739 | -7.7953 | -35.0705 | 8.1782 | 0.10344 | 0.3829 | 0.094517 | 0.094505 | 0.094517 | 1.0003 | -58.6989 | 1 | -59.3612 | 0.05912 | -35.1739 | -40.3563 | 7.7953 | -26.6459
78900902 | 299.0165 | -192.6548 | -293.4304 | 243.1817 | 5.5861 | 50.5269 | 0.44634 | 0.44616 | 0.44634 | 0.92022 | -27.5032 | 0.98633 | -34.392 | 0.12093 | -299.0165 | -294.0276 | 192.6548 | 156.4373
79900938 | 212.806 | -206.2716 | -208.9911 | 246.7246 | 3.8148 | 40.453 | 0.37188 | 0.37165 | 0.37188 | 0.92022 | -27.5032 | 1.0046 | -33.1632 | 0.132 | -212.806 | -191.6675 | 206.2716 | 167.0373
809009932 | 623.3775 | -171.9843 | -613.1066 | 297.4291 | 10.2709 | 125.4448 | 0.81144 | 0.81136 | 0.81144 | 0.92022 | -27.5032 | 0.9698 | -37.9725 | 0.10661 | -623.3775 | -684.0527 | 171.9843 | 61.7092
819017212 | 82.0694 | -15.1057 | -80.0233 | 24.1877 | 2.0461 | 9.0821 | 0.2387 | 0.2387 | 0.2387 | 0.91743 | -29.1156 | 0.91912 | -35.5133 | 0.091831 | -82.0694 | -107.3323 | 15.1057 | 16.7165
829017219 | 13.0619 | 4.4544 | -13 | -4.2 | 0.061922 | 0.25438 | 0.039477 | 0.03949 | 0.03949 | 0.91743 | -29.1156 | 0.90788 | -30.1002 | 0.076818 | -13.0619 | -13.0479 | -4.4544 | 17.0664
83902938 | -291.0117 | -201.3776 | 291.9385 | 211.3618 | 0.92682 | 9.9842 | 0.41431 | 0.41427 | 0.41431 | 0.98633 | -34.392 | 1.0046 | -33.1632 | 0.11368 | 291.0117 | 321.4078 | 201.3776 | 62.0089
849029932 | 210.3686 | 41.9915 | -209.0249 | -28.5058 | 1.3437 | 13.4856 | 0.25114 | 0.25118 | 0.25118 | 0.98633 | -34.392 | 0.9698 | -37.9725 | 0.080426 | -210.3686 | -255.4242 | -41.9915 | 115.9621
85903904 | 25.3755 | -43.221 | -25.0069 | 44.7991 | 0.36859 | 1.5781 | 0.13249 | 0.13247 | 0.13249 | 0.99272 | -37.0445 | 1.0164 | -38.2971 | 0.18503 | -25.3755 | -0.5892 | 43.221 | -18.5106
86903907 | -88.5547 | -92.0059 | 91.1905 | 103.5534 | 2.6357 | 11.5475 | 0.33758 | 0.33756 | 0.33758 | 0.99272 | -37.0445 | 1.0727 | -34.5039 | 0.15843 | 88.5547 | 86.6174 | 92.0059 | 1.5984
87903928 | 25.4505 | -39.0462 | -25.1313 | 40.4626 | 0.31921 | 1.4163 | 0.12321 | 0.12319 | 0.12321 | 0.99272 | -37.0445 | 1.0147 | -38.3027 | 0.18162 | -25.4505 | -2.2081 | 39.0462 | -16.9459
889037213 | 117.9469 | 17.8482 | -116.7609 | -12.8802 | 1.186 | 4.9681 | 0.31535 | 0.31538 | 0.31538 | 0.99272 | -37.0445 | 0.97748 | -39.3973 | 0.098033 | -117.9469 | -113.5889 | -17.8482 | 36.0501
89904939 | -379.8627 | 2.6542 | 382.0272 | 12.7792 | 2.1646 | 15.4334 | 0.98083 | 0.98083 | 0.98083 | 1.0164 | -38.2971 | 1.0227 | -35.9798 | 0.14838 | 379.8627 | 261.1784 | -2.6542 | 50.4494
909077218 | -76.8075 | 60.4521 | 77.6653 | -56.6783 | 0.85785 | 3.7738 | 0.23912 | 0.23917 | 0.23917 | 1.0727 | -34.5039 | 1.055 | -32.4056 | 0.16492 | 76.8075 | 56.16 | -60.4521 | 20.4767
91912953 | -337.0305 | 86.3453 | 338.3932 | -78.7523 | 1.3626 | 7.593 | 0.89661 | 0.89662 | 0.89662 | 1.0183 | -40.5572 | 1.0169 | -39.2877 | 0.18497 | 337.0305 | 173.0754 | -86.3453 | 84.8247
92918912 | -239.7565 | 53.9852 | 245.8656 | -29.5562 | 6.1092 | 24.4289 | 0.63818 | 0.63818 | 0.63818 | 1.0106 | -46.3936 | 1.0183 | -40.5572 | 0.30477 | 239.7565 | 81.3996 | -53.9852 | 12.2
939182952 | 158.3565 | -66.1852 | -152.8325 | 90.3538 | 5.5239 | 24.1686 | 0.44569 | 0.44567 | 0.44569 | 1.0106 | -46.3936 | 1.0455 | -54.3062 | 0.036774 | -158.3565 | -474.8556 | 66.1852 | 38.2318
94928904 | -14.8687 | -52.4626 | 14.8884 | 52.551 | 0.01969 | 0.088444 | 0.14103 | 0.14103 | 0.14103 | 1.0147 | -38.3027 | 1.0164 | -38.2971 | 0.13849 | 14.8687 | 37.8551 | 52.4626 | -15.2218
95932814 | 57.8348 | -62.8768 | -57.6129 | 63.8993 | 0.22188 | 1.0224 | 0.23852 | 0.23852 | 0.23852 | 0.93995 | -40.7335 | 0.94664 | -41.3039 | 0.11917 | -57.8348 | -74.3685 | 62.8768 | 34.0219
969321916 | 182.7374 | -52.7543 | -168.5251 | 113.6425 | 14.2123 | 60.8882 | 0.53103 | 0.53101 | 0.53103 | 0.93995 | -40.7335 | 1.0045 | -58.6294 | 0.092112 | -182.7374 | -228.7083 | 52.7543 | -45.2824
979327212 | -63.543 | 35.3543 | 65.0233 | -28.7877 | 1.4803 | 6.5665 | 0.20302 | 0.20304 | 0.20304 | 0.93995 | -40.7335 | 0.91912 | -35.5133 | 0.092376 | 63.543 | 88.2506 | -35.3543 | -2.0975
98935907 | 14.1525 | 20.5842 | -13.9745 | -19.6237 | 0.17798 | 0.9605 | 0.058866 | 0.058936 | 0.058936 | 1.1136 | -33.5109 | 1.0727 | -34.5039 | 0.068273 | -14.1525 | -15.9189 | -20.5842 | 3.2058
99935911 | 63.8475 | 56.3214 | -62.9658 | -51.3968 | 0.88165 | 4.9246 | 0.20063 | 0.20066 | 0.20066 | 1.1136 | -33.5109 | 1.063 | -35.7115 | 0.12385 | -63.8475 | -62.0887 | -56.3214 | -14.564
100939907 | -119.2993 | -155.4147 | 120.8916 | 166.1766 | 1.5923 | 10.7619 | 0.50274 | 0.50273 | 0.50274 | 1.0227 | -35.9798 | 1.0727 | -34.5039 | 0.17783 | 119.2993 | 105.0533 | 155.4147 | 46.1519
101939911 | -12.6382 | -34.9748 | 12.9658 | 36.3968 | 0.32768 | 1.422 | 0.095425 | 0.095384 | 0.095425 | 1.0227 | -35.9798 | 1.063 | -35.7115 | 0.12173 | 12.6382 | 11.4358 | 34.9748 | 29.6907
1029397213 | 191.7956 | 92.1929 | -188.2391 | -77.1198 | 3.5564 | 15.073 | 0.54605 | 0.54615 | 0.54615 | 1.0227 | -35.9798 | 0.97748 | -39.3973 | 0.10768 | -191.7956 | -195.1224 | -92.1929 | 65.6308
103953904 | -350.3932 | 76.7523 | 351.4857 | -70.6499 | 1.0925 | 6.1024 | 0.92569 | 0.92569 | 0.92569 | 1.0169 | -39.2877 | 1.0164 | -38.2971 | 0.18175 | 350.3932 | 185.4694 | -76.7523 | 84.7257
10498026 | -339.888 | 143.1129 | 345.6452 | -73.6236 | 5.7571 | 69.4893 | 0.43581 | 0.43594 | 0.43594 | 0.97712 | 20.6405 | 0.93607 | 31.5024 | 0.10978 | 339.888 | 300.5696 | -143.1129 | 175.0602
105980240 | -450.4015 | 14.9597 | 455.2683 | 34.6826 | 4.8668 | 49.6423 | 0.53255 | 0.53255 | 0.53255 | 0.97712 | 20.6405 | 0.99 | 26.9212 | 0.10606 | 450.4015 | 408.2937 | -14.9597 | -5.329
106980986 | 865.4345 | 261.2519 | -831.7407 | 150.7674 | 33.6938 | 412.0193 | 1.0683 | 1.0683 | 1.0683 | 0.97712 | 20.6405 | 0.91364 | -6.4517 | 0.1221 | -865.4345 | -764.8434 | -261.2519 | 100.4579
1079817201 | -139.4624 | 189.925 | 142.5072 | -165.9634 | 3.0448 | 23.9616 | 0.57401 | 0.57407 | 0.57407 | 1.0773 | 21.5349 | 1 | 25.9014 | 0.14239 | 139.4624 | 136.9914 | -189.925 | -61.6411
1089817202 | -106.7389 | 30.8683 | 107.8259 | -19.3661 | 1.087 | 11.5022 | 0.27068 | 0.2707 | 0.2707 | 1.0773 | 21.5349 | 1.0621 | 27.5001 | 0.122 | 106.7389 | 88.9887 | -30.8683 | 9.8837
109986987 | 831.7407 | -150.7674 | -803.2205 | 453.6051 | 28.5202 | 302.8377 | 1.0683 | 1.0682 | 1.0683 | 0.91364 | -6.4517 | 0.99713 | -25.6465 | 0.123 | -831.7407 | -742.3606 | 150.7674 | 175.7766
110987938 | 517.8344 | -44.276 | -511.4123 | 112.2906 | 6.4221 | 68.0147 | 0.60185 | 0.60182 | 0.60185 | 0.99713 | -25.6465 | 1.0046 | -33.1632 | 0.11249 | -517.8344 | -462.0292 | 44.276 | 133.649
1119887218 | 118.0745 | -45.0153 | -116.5653 | 51.6783 | 1.5091 | 6.663 | 0.3172 | 0.31717 | 0.3172 | 1.0455 | -29.3525 | 1.055 | -32.4056 | 0.12924 | -118.0745 | -96.1618 | 45.0153 | 33.8909
1121621240 | 121.3267 | -76.2307 | -120.9544 | 79.8715 | 0.37232 | 3.6408 | 0.16915 | 0.16906 | 0.16915 | 0.97817 | 28.2635 | 0.99 | 26.9212 | 0.14185 | -121.3267 | -72.4976 | 76.2307 | 74.9363
11316301621 | 129.6994 | 66.8591 | -128.8385 | -58.4218 | 0.86089 | 8.4373 | 0.16682 | 0.16699 | 0.16699 | 1.01 | 31.2639 | 0.97817 | 28.2635 | 0.071788 | -129.6994 | -106.1961 | -66.8591 | 172.7436
11416319917 | 237.772 | 38.6598 | -235.2645 | -13.4571 | 2.5075 | 25.2027 | 0.27816 | 0.2782 | 0.2782 | 1 | 30.7928 | 0.97807 | 24.7513 | 0.075123 | -237.772 | -252.2763 | -38.6598 | 211.1855
11616601630 | 168.8849 | -90.4105 | -168.8575 | 90.688 | 0.027371 | 0.27749 | 0.21913 | 0.21913 | 0.21913 | 1.0094 | 31.3425 | 1.01 | 31.2639 | 0.091734 | -168.8849 | -116.021 | 90.4105 | -98.7912
11516601630 | 125.8627 | -67.7083 | -125.8419 | 67.9115 | 0.020848 | 0.20325 | 0.16349 | 0.16348 | 0.16349 | 1.0094 | 31.3425 | 1.01 | 31.2639 | 0.090996 | -125.8627 | -155.2313 | 67.7083 | -135.2662
11716601631 | 52.8695 | 41.82 | -52.772 | -41.0916 | 0.097551 | 0.72839 | 0.077112 | 0.07723 | 0.07723 | 1.0094 | 31.3425 | 1 | 30.7928 | 0.042892 | -52.8695 | -67.4436 | -41.82 | 143.3129
11816601636 | -350.5701 | 29.693 | 353 | 28.1377 | 2.4299 | 57.8307 | 0.40246 | 0.40246 | 0.40246 | 1.0094 | 31.3425 | 1.016 | 40.8201 | 0.084021 | 350.5701 | 350.5814 | -29.693 | 201.8887
11918171850 | -204.517 | 30.1323 | 205.1644 | -23.5528 | 0.64738 | 6.5795 | 0.25118 | 0.2512 | 0.2512 | 0.95032 | 23.2233 | 0.94928 | 25.0829 | 0.082514 | 204.517 | 238.2275 | -30.1323 | -15.3538
12018521853 | 49.5506 | 51.9973 | -49.3657 | -50.0855 | 0.18487 | 1.9118 | 0.084712 | 0.084974 | 0.084974 | 0.97905 | 24.1062 | 0.95563 | 22.9696 | 0.040777 | -49.5506 | -16.5764 | -51.9973 | 182.3558
12118531817 | -40.0585 | 61.9878 | 40.1086 | -61.5282 | 0.050139 | 0.45957 | 0.089179 | 0.089242 | 0.089242 | 0.95563 | 22.9696 | 0.95032 | 23.2233 | 0.10203 | 40.0585 | 58.4854 | -61.9878 | 50.4862
12218539917 | -88.5758 | -51.9023 | 88.9645 | 55.6571 | 0.38868 | 3.7548 | 0.12405 | 0.12389 | 0.12405 | 0.95563 | 22.9696 | 0.97807 | 24.7513 | 0.05493 | 88.5758 | 102.9545 | 51.9023 | 170.8661
1231916903 | -194.8872 | 93.4304 | 213.0592 | -15.0291 | 18.172 | 78.4013 | 0.56462 | 0.56463 | 0.56463 | 1.0045 | -58.6294 | 0.99272 | -37.0445 | 0.09144 | 194.8872 | 225.3336 | -93.4304 | -27.2484
12419167214 | 79.9946 | -3.8023 | -79.2304 | 7.0859 | 0.76425 | 3.2836 | 0.20922 | 0.20922 | 0.20922 | 1.0045 | -58.6294 | 0.9978 | -61.0243 | 0.042205 | -79.9946 | -171.2869 | 3.8023 | 62.1524
12519167217 | -111.5824 | 93.6939 | 113.9948 | -83.5543 | 2.4125 | 10.1396 | 0.38064 | 0.38066 | 0.38066 | 1.0045 | -58.6294 | 0.97441 | -54.8467 | 0.10395 | 111.5824 | 129.0617 | -93.6939 | -29.7727
12629187215 | 67.3852 | -37.2259 | -66.0411 | 42.9839 | 1.3441 | 5.758 | 0.20341 | 0.20338 | 0.20341 | 0.9932 | -46.196 | 1.0168 | -50.3554 | 0.053034 | -67.3852 | -134.6938 | 37.2259 | 60.6851
12729187217 | 299.4279 | -9.67 | -288.9948 | 53.5543 | 10.4331 | 43.8843 | 0.79159 | 0.79159 | 0.79159 | 0.9932 | -46.196 | 0.97441 | -54.8467 | 0.095056 | -299.4279 | -317.8113 | 9.67 | -38.3628
1282919800 | 269.4228 | -146.2231 | -267.1203 | 172.496 | 2.3025 | 26.2729 | 0.35771 | 0.35759 | 0.35771 | 0.98953 | -42.4723 | 1.0268 | -46.8677 | 0.11193 | -269.4228 | -259.3142 | 146.2231 | 116.0323
12929192921 | -223.3344 | -86.9813 | 225 | 101.837 | 1.6656 | 14.8558 | 0.27968 | 0.27959 | 0.27968 | 0.98953 | -42.4723 | 1.02 | -39.3552 | 0.091438 | 223.3344 | 223.5653 | 86.9813 | 49.9796
1302925843 | 122.1687 | -19.847 | -119.6841 | 34.8975 | 2.4846 | 15.0504 | 0.31069 | 0.31068 | 0.31069 | 1.0455 | -44.7786 | 1.0531 | -51.8154 | 0.11748 | -122.1687 | -98.2217 | 19.847 | 38.1036
13129527214 | 247.8301 | 52.485 | -240.7696 | -22.0859 | 7.0604 | 30.3991 | 0.63591 | 0.63591 | 0.63591 | 1.0455 | -54.3062 | 0.9978 | -61.0243 | 0.13453 | -247.8301 | -156.7672 | -52.485 | -96.4796
13229527215 | -64.6975 | 48.7379 | 66.0411 | -42.9839 | 1.3436 | 5.754 | 0.20333 | 0.20338 | 0.20338 | 1.0455 | -54.3062 | 1.0168 | -50.3554 | 0.05751 | 64.6975 | 126.4672 | -48.7379 | -34.4636
13347034727 | -423.918 | 76.8217 | 430.6155 | -14.2344 | 6.6975 | 62.5873 | 0.49747 | 0.4975 | 0.4975 | 1 | 16.611 | 1 | 25.0244 | 0.084012 | 423.918 | 488.4949 | -76.8217 | 35.5221
13447034782 | 841.918 | -78.385 | -836.3127 | 124.6602 | 5.6053 | 46.2753 | 0.97637 | 0.97636 | 0.97637 | 1 | 16.611 | 1 | 13.4483 | 0.094094 | -841.918 | -906.4949 | 78.385 | 152.2835
13547271852 | 50.7605 | 54.6762 | -50.5506 | -52.9973 | 0.20986 | 1.6789 | 0.086148 | 0.08638 | 0.08638 | 1 | 25.0244 | 0.97905 | 24.1062 | 0.048728 | -50.7605 | -17.5924 | -54.6762 | 133.1686
13647824705 | 876.2572 | -104.9654 | -871.5842 | 164.0993 | 4.673 | 59.1339 | 1.019 | 1.019 | 1.019 | 1 | 13.4483 | 1.005 | 9.6128 | 0.09775 | -876.2572 | -908.6722 | 104.9654 | 177.2567
137478210000 | 399.0555 | -212.0984 | -397.6015 | 233.1276 | 1.454 | 21.0292 | 0.52183 | 0.52177 | 0.52183 | 1 | 13.4483 | 1.02 | 11.0432 | 0.094957 | -399.0555 | -483.1505 | 212.0984 | 20.7034
13847854799 | -565.1166 | 88.693 | 573.2741 | -17.0453 | 8.1575 | 71.6477 | 0.66223 | 0.66225 | 0.66225 | 0.99743 | -0.094562 | 1 | 7.1409 | 0.080494 | 565.1166 | 684.9655 | -88.693 | -96.1812
1394790577 | -91.2384 | 84.5851 | 91.5323 | -81.4051 | 0.2939 | 3.18 | 0.13921 | 0.13935 | 0.13935 | 1.032 | 0 | 1.015 | 1.2495 | 0.047161 | 91.2384 | 221.6858 | -84.5851 | 41.4318
14047904785 | 20.146 | 132.9646 | -19.6834 | -128.693 | 0.46266 | 4.2716 | 0.15047 | 0.15072 | 0.15072 | 1.032 | 0 | 0.99743 | -0.094562 | 0.079387 | -20.146 | 99.8927 | -132.9646 | 86.6544
1414799576 | 135.5889 | -11.5502 | -135.2245 | 15.0979 | 0.36439 | 3.5477 | 0.15713 | 0.15711 | 0.15713 | 1 | 7.1409 | 1 | 5.574 | 0.078328 | -135.5889 | -125.0771 | 11.5502 | 124.0541
1427223805 | 3.8933 | -44.8712 | -3.4964 | 46.3483 | 0.39688 | 1.4771 | 0.1157 | 0.11567 | 0.1157 | 1.0216 | -47.4657 | 1.0545 | -48.1119 | 0.087958 | -3.8933 | 1.666 | 44.8712 | 52.6148
14372232918 | -17.8933 | 42.8712 | 18.3157 | -41.2973 | 0.42246 | 1.5739 | 0.11934 | 0.11937 | 0.11937 | 1.0216 | -47.4657 | 0.9932 | -46.196 | 0.073176 | 17.8933 | 12.334 | -42.8712 | -50.6149
1447224801 | -74.3974 | 0.19884 | 75.877 | 5.5542 | 1.4796 | 5.753 | 0.19193 | 0.19192 | 0.19193 | 1.0173 | -53.5647 | 1.0403 | -49.2059 | 0.091631 | 74.3974 | 78.8309 | -0.19884 | -9.5579
1457228840 | 44.4476 | 18.9235 | -43.5841 | -15.1726 | 0.86351 | 3.7509 | 0.11915 | 0.11918 | 0.11918 | 1.064 | -51.6444 | 1.0162 | -55.5444 | 0.10221 | -44.4476 | -43.527 | -18.9235 | 20.0798
14699322919 | 632.6895 | -202.0827 | -627.399 | 256.1203 | 5.2905 | 54.0376 | 0.79081 | 0.79077 | 0.79081 | 0.9698 | -37.9725 | 0.98953 | -42.4723 | 0.10031 | -632.6895 | -701.9235 | 202.0827 | 51.0808
147100004799 | 947.6015 | 239.7027 | -942.863 | -171.3097 | 4.7386 | 68.393 | 1.1065 | 1.1065 | 1.1065 | 1.02 | 11.0432 | 1 | 7.1409 | 0.09202 | -947.6015 | -1061.5629 | -239.7027 | -9.6155

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
12539 | 123.2407 | -428.3477 | -122.8951 | 453.8294 | 0.34565 | 25.4817 | 0.54998 | 1.2526 | 0.93581 | 31.8309 | 0.98508 | 31.001 | 59.5877
22551 | -2781.8811 | 764.9048 | 2816 | 1597.2271 | 34.1189 | 2362.1319 | 3.56 | 93.4567 | 0.93581 | 31.8309 | 1 | 76.7637 | 513.8787
32860 | -934.8988 | -261.5605 | 939 | 534.973 | 4.1012 | 273.4126 | 1.1876 | 31.1972 | 0.94391 | 32.868 | 1 | 46.8582 | 171.54
43130 | -792.8531 | -112.7422 | 797 | 353.9365 | 4.1469 | 241.1943 | 0.95801 | 25.1741 | 0.96524 | 32.4105 | 1 | 48.1416 | 218.0138
53133 | -267.9649 | -188.0404 | 268.4737 | 207.4297 | 0.50879 | 19.3893 | 0.39161 | 0.82999 | 0.96524 | 32.4105 | 1.0727 | 34.7613 | 42.5355
63950 | -473.9523 | -438.655 | 476 | 544.0151 | 2.0477 | 105.3601 | 1.7204 | 20.8672 | 0.98508 | 31.001 | 1 | 36.9379 | 114.7399
7129130 | 290.6402 | -185.2504 | -290.1073 | 213.0201 | 0.53288 | 27.7697 | 0.38189 | 0.8731 | 1.0421 | 16.3918 | 1.0818 | 12.7999 | 69.4248
8129130 | 290.6402 | -185.2504 | -290.1073 | 213.0201 | 0.53288 | 27.7697 | 0.38189 | 0.8731 | 1.0421 | 16.3918 | 1.0818 | 12.7999 | 69.4248
92242925 | 6.5074 | -116.6948 | -6.1687 | 122.5724 | 0.33874 | 5.8776 | 0.13231 | 0.30807 | 1.02 | -44.6793 | 1.0455 | -44.7786 | 23.4783
10240241 | -167.1569 | -57.277 | 167.5465 | 67.0512 | 0.38953 | 9.7741 | 0.20609 | 0.45105 | 0.99 | 26.9212 | 1.05 | 29.0297 | 35.9368
11240241 | -167.1569 | -57.277 | 167.5465 | 67.0512 | 0.38953 | 9.7741 | 0.20609 | 0.45105 | 0.99 | 26.9212 | 1.05 | 29.0297 | 35.9368
12325310 | 309.1988 | -254.9948 | -308.2024 | 301.9205 | 0.99644 | 46.9257 | 0.51903 | 1.1321 | 0.89162 | 10.1193 | 1.0001 | 5.4815 | 90.2007
13355356 | -182.0432 | -78.1032 | 183 | 107.606 | 0.9568 | 29.5029 | 0.49799 | 1.013 | 1.0439 | 1.9518 | 1.1 | 7.5448 | 88.4552
14467455 | -15.2411 | -65.4492 | 15.4 | 69.6925 | 0.15888 | 4.2433 | 0.16888 | 0.34056 | 1.0443 | -24.4548 | 1.1 | -23.8504 | 51.9082
15469468 | 12.7741 | -105.7059 | -12.5054 | 111.1978 | 0.26873 | 5.492 | 0.14116 | 0.31284 | 0.87095 | -5.3228 | 0.93868 | -5.5566 | 24.9254
16473472 | 79.2792 | -57.763 | -79 | 67.7353 | 0.27916 | 9.9723 | 0.26059 | 0.49653 | 0.98783 | -8.8572 | 1.1 | -13.1604 | 83.2503
17480466 | 190.6263 | -227.2884 | -190.0028 | 250.7188 | 0.62353 | 23.4304 | 0.35325 | 0.77286 | 0.96967 | -12.482 | 1.0682 | -14.9564 | 61.5775
18800801 | 189.0572 | -76.5763 | -188.8038 | 87.4102 | 0.25341 | 10.834 | 0.22939 | 0.52485 | 1.0268 | -46.8677 | 1.0403 | -49.2059 | 41.734
19830831 | 251.3187 | -175.2941 | -250.8858 | 198.4364 | 0.43288 | 23.1423 | 0.3386 | 0.77924 | 1.0449 | -47.8121 | 1.0773 | -50.5319 | 61.9617
20830831 | 251.3187 | -175.2941 | -250.8858 | 198.4364 | 0.43288 | 23.1423 | 0.3386 | 0.77924 | 1.0449 | -47.8121 | 1.0773 | -50.5319 | 61.9617
21900901 | 98.3865 | -3.7734 | -98.1313 | 8.6513 | 0.25522 | 4.8779 | 0.12355 | 0.2818 | 0.92022 | -27.5032 | 0.91743 | -29.1156 | 22.4688
22902903 | 187.0367 | -41.8978 | -186.6387 | 52.127 | 0.39808 | 10.2292 | 0.22439 | 0.51227 | 0.98633 | -34.392 | 0.99272 | -37.0445 | 40.8149
23902903 | 187.0367 | -41.8978 | -186.6387 | 52.127 | 0.39808 | 10.2292 | 0.22439 | 0.51227 | 0.98633 | -34.392 | 0.99272 | -37.0445 | 40.8149
24904905 | 38.4954 | -29.3544 | -38 | 38.573 | 0.49544 | 9.2186 | 0.125 | 0.25836 | 1.0164 | -38.2971 | 1.1 | -40.2221 | 22.5612
25912913 | 91.1649 | -56.7891 | -91 | 63.1333 | 0.16489 | 6.3442 | 0.2768 | 0.52847 | 1.0183 | -40.5572 | 1.1 | -42.9445 | 44.3023
26938939 | 214.2324 | -285.1885 | -213.4427 | 316.9436 | 0.78976 | 31.7551 | 0.40998 | 0.9805 | 1.0046 | -33.1632 | 1.0227 | -35.9798 | 74.5754
27938939 | 214.2324 | -285.1885 | -213.4427 | 316.9436 | 0.78976 | 31.7551 | 0.40998 | 0.9805 | 1.0046 | -33.1632 | 1.0227 | -35.9798 | 74.5754
28980981 | -75.145 | -419.3245 | 76.2013 | 468.3228 | 1.0563 | 48.9983 | 0.50343 | 1.1559 | 0.97712 | 20.6405 | 1.0773 | 21.5349 | 92.0935
29987988 | 285.3861 | -409.3291 | -284.0745 | 471.2359 | 1.3117 | 61.9068 | 0.57785 | 1.3812 | 0.99713 | -25.6465 | 1.0455 | -29.3525 | 105.0528
3029192918 | 290.6553 | -11.458 | -290.0644 | 31.5966 | 0.59083 | 20.1386 | 0.33943 | 0.77097 | 0.98953 | -42.4723 | 0.9932 | -46.196 | 58.6742
3129192918 | 290.6553 | -11.458 | -290.0644 | 31.5966 | 0.59083 | 20.1386 | 0.33943 | 0.77097 | 0.98953 | -42.4723 | 0.9932 | -46.196 | 58.6742
329932932 | 189.4421 | -66.8405 | -189.0292 | 78.2769 | 0.41285 | 11.4364 | 0.23919 | 0.57123 | 0.9698 | -37.9725 | 0.93995 | -40.7335 | 43.4465

## res_ext_grid
| p_mw | q_mvar
4790 | -71.0924 | 217.5498

## res_load
| p_mw | q_mvar
30 | 12 | 3
31 | 430 | 120
33 | 522.8 | 302
39 | 360 | 50
50 | 25 | 15
51 | 80 | 15
60 | 22 | 8
63 | 0 | 0
130 | 1050 | 98
147 | 232 | 10
175 | 255 | 60
180 | 103.5 | -99.4
224 | 2500 | 0
241 | 840 | 183
306 | 20.5 | 5.1
310 | 67 | 20
356 | 394 | 152
455 | 80.6 | 35.1
465 | 33 | 3.2
466 | 130 | 32
469 | 10 | 0
472 | 222 | 44.7
475 | 6.4 | 2.1
576 | 304 | -25
577 | 256 | -33.8
590 | 154 | 55
801 | 265 | 20
805 | 322 | 88
814 | 8 | 2
831 | 386.3 | 59.8
839 | 11.3 | 4.5
840 | 20 | 4
842 | 30 | 9.1
843 | 195.3 | 45.3
862 | 154 | 44
865 | 18 | 3
869 | 18 | 6
901 | 3 | 2
903 | 80 | 67.2
905 | 220 | 50
907 | 55.7 | 14
911 | 50 | 15
913 | 670 | 279
918 | 81.4 | 12.2
928 | 40 | 12
932 | 12 | 2
953 | 12 | 2
981 | 180 | 50
988 | 202 | 27
1621 | 175 | 79
1630 | 368 | 60
1631 | 5 | 165
1636 | 2754 | 200
1817 | 385 | 114
1850 | 174 | 11
1852 | 1 | 1
1853 | 178 | 40
1916 | 825 | 102
2918 | 195 | 25
2921 | 2295 | 25
2925 | 660 | 70
2952 | 420 | 76.2
4703 | 140 | -35
4705 | 716 | -196
4727 | 16 | 55
4785 | 584.8 | 40
4799 | 280 | 66.7
7201 | 135 | 40
7202 | 24 | 9
7203 | 173 | 49.7
7204 | 38 | 18.8
7205 | 9.1 | 1.3
7206 | 54 | 30.4
7208 | 1183.4 | 452.2
7209 | 7.4 | 2.4
7210 | 20.3 | 7.9
7211 | 18 | 5.3
7212 | 15 | 4.6
7213 | 305 | 90
7214 | 320 | 15
7216 | 55.1 | 16.2
7217 | 175 | 30
7218 | 38.9 | 5
7219 | 13 | 4.2
7221 | 207 | 42.9
7223 | 14 | 2
7224 | 43 | 6.3
7225 | 29.9 | 7.7
7226 | 20 | 3
7227 | 93 | -10
7228 | 20 | 3.4
7229 | 24 | 19.3
9917 | 146.3 | -42.2

## res_shunt
| p_mw | q_mvar | vm_pu
25 | 0 | 0 | 0.93581
26 | 0 | 0 | 0.93607
31 | 0 | 0 | 0.96524
129 | 0 | 0 | 1.0421
147 | 0 | 0 | 1.01
175 | 0 | 0 | 0.97043
180 | 0 | 0 | 1.0786
469 | 0 | 0 | 0.87095
480 | 0 | 0 | 0.96967
576 | 0 | 0 | 1
577 | 0 | 0 | 1.015
590 | 0 | 0 | 0.99395
800 | 0 | 0 | 1.0268
869 | 0 | 0 | 1.0003
900 | 0 | 0 | 0.92022
902 | 0 | 0 | 0.98633
938 | 0 | 0 | 1.0046
980 | 0 | 0 | 0.97712
986 | 0 | 0 | 0.91364
1621 | 0 | 0 | 0.97817
1630 | 0 | 0 | 1.01
1631 | 0 | 0 | 1
1660 | 0 | 0 | 1.0094
1817 | 0 | 0 | 0.95032
1850 | 0 | 0 | 0.94928
1852 | 0 | 0 | 0.97905
1853 | 0 | 0 | 0.95563
2919 | 0 | 0 | 0.98953
2921 | 0 | 0 | 1.02
4703 | 0 | 0 | 1
4705 | 0 | 0 | 1.005
4727 | 0 | 0 | 1
4790 | 0 | 0 | 1.032
7227 | 0 | 0 | 0.95131
9917 | 0 | 0 | 0.97807
9932 | 0 | 0 | 0.9698

## res_gen
| p_mw | q_mvar | va_degree | vm_pu
30 | 809 | 356.9365 | 48.1416 | 1
33 | 1120 | 675.354 | 34.7613 | 1.0727
50 | 501 | 559.0151 | 36.9379 | 1
51 | 2896 | 1612.2271 | 76.7637 | 1
60 | 961 | 542.973 | 46.8582 | 1
63 | 0 | 0 | 0 | 0
130 | 468 | 702.96 | 12.7999 | 1.0818
147 | 250 | 430.5873 | 21.1354 | 1.01
224 | 2934 | -339.6164 | -44.6793 | 1.02
241 | 1301 | 408.9513 | 29.0297 | 1.05
356 | 577 | 259.606 | 7.5448 | 1.1
455 | 96 | 104.7925 | -23.8504 | 1.1
466 | 206 | 397.2237 | -14.9564 | 1.0682
472 | 143 | 112.4353 | -13.1604 | 1.1
576 | 94 | 59.7072 | 5.574 | 1
805 | 470 | 292.7034 | -48.1119 | 1.0545
831 | 127 | 650.8376 | -50.5319 | 1.0773
862 | 53 | 100.3744 | -59.8936 | 1
905 | 182 | 88.573 | -40.2221 | 1.1
907 | 177 | 324.5584 | -34.5039 | 1.0727
913 | 579 | 342.1333 | -42.9445 | 1.1
935 | 78 | 76.9056 | -33.5109 | 1.1136
939 | 15 | 548.4699 | -35.9798 | 1.0227
981 | 10 | 739.116 | 21.5349 | 1.0773
988 | 36 | 453.2206 | -29.3525 | 1.0455
1630 | 203 | 285.4587 | 31.2639 | 1.01
1631 | 190 | 162.5682 | 30.7928 | 1
1636 | 3107 | 228.1377 | 40.8201 | 1.016
1916 | 430 | 398.9645 | -58.6294 | 1.0045
2921 | 2520 | 126.837 | -39.3552 | 1.02
2925 | 776 | 172.7253 | -44.7786 | 1.0455
2952 | 450.3 | 267.7767 | -54.3062 | 1.0455
4703 | 558 | -36.5633 | 16.611 | 1
4727 | 696 | 50.3736 | 25.0244 | 1
4782 | 439 | -192.4035 | 13.4483 | 1
4799 | 46 | -133.2053 | 7.1409 | 1
7201 | 153 | -206.7942 | 25.9014 | 1
7203 | 12 | -56.7613 | 31.4927 | 1
7204 | 30 | -12.1147 | 21.4336 | 1
7208 | 946 | 884.7056 | 1.6772 | 1.0591
7226 | 13 | 4.119 | -59.3612 | 1
10000 | 550 | 472.8303 | 11.0432 | 1.02

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | gen | name | object
16 | gen | bus | uint32
17 | gen | p_mw | float64
18 | gen | vm_pu | float64
19 | gen | sn_mva | float64
20 | gen | min_q_mvar | float64
21 | gen | max_q_mvar | float64
22 | gen | scaling | float64
23 | gen | slack | bool
24 | gen | in_service | bool
25 | gen | slack_weight | float64
26 | gen | type | object
27 | gen | power_station_trafo | float64
28 | shunt | bus | uint32
29 | shunt | name | object
30 | shunt | q_mvar | float64
31 | shunt | p_mw | float64
32 | shunt | vn_kv | float64
33 | shunt | step | uint32
34 | shunt | max_step | uint32
35 | shunt | in_service | bool
36 | ext_grid | name | object
37 | ext_grid | bus | uint32
38 | ext_grid | vm_pu | float64
39 | ext_grid | va_degree | float64
40 | ext_grid | slack_weight | float64
41 | ext_grid | in_service | bool
42 | line | name | object
43 | line | std_type | object
44 | line | from_bus | uint32
45 | line | to_bus | uint32
46 | line | length_km | float64
47 | line | r_ohm_per_km | float64
48 | line | x_ohm_per_km | float64
49 | line | c_nf_per_km | float64
50 | line | g_us_per_km | float64
51 | line | max_i_ka | float64
52 | line | df | float64
53 | line | parallel | uint32
54 | line | type | object
55 | line | in_service | bool
56 | trafo | name | object
57 | trafo | std_type | object
58 | trafo | hv_bus | uint32
59 | trafo | lv_bus | uint32
60 | trafo | sn_mva | float64
61 | trafo | vn_hv_kv | float64
62 | trafo | vn_lv_kv | float64
63 | trafo | vk_percent | float64
64 | trafo | vkr_percent | float64
65 | trafo | pfe_kw | float64
66 | trafo | i0_percent | float64
67 | trafo | shift_degree | float64
68 | trafo | tap_side | object
69 | trafo | tap_neutral | float64
70 | trafo | tap_min | float64
71 | trafo | tap_max | float64
72 | trafo | tap_step_percent | float64
73 | trafo | tap_step_degree | float64
74 | trafo | tap_pos | float64
75 | trafo | tap_phase_shifter | bool
76 | trafo | parallel | uint32
77 | trafo | df | float64
78 | trafo | in_service | bool
79 | trafo | pt_percent | float64
80 | trafo | oltc | object
81 | trafo | Unnamed: 26 | float64
82 | trafo | Unnamed: 27 | int64
83 | measurement | name | object
84 | measurement | measurement_type | object
85 | measurement | element_type | object
86 | measurement | element | int64
87 | measurement | value | float64
88 | measurement | std_dev | float64
89 | measurement | side | float64
90 | res_bus | vm_pu | float64
91 | res_bus | va_degree | float64
92 | res_bus | p_mw | float64
93 | res_bus | q_mvar | float64
94 | res_line | p_from_mw | float64
95 | res_line | q_from_mvar | float64
96 | res_line | p_to_mw | float64
97 | res_line | q_to_mvar | float64
98 | res_line | pl_mw | float64
99 | res_line | ql_mvar | float64
100 | res_line | i_from_ka | float64
101 | res_line | i_to_ka | float64
102 | res_line | i_ka | float64
103 | res_line | vm_from_pu | float64
104 | res_line | va_from_degree | float64
105 | res_line | vm_to_pu | float64
106 | res_line | va_to_degree | float64
107 | res_line | loading_percent | float64
108 | res_trafo | p_hv_mw | float64
109 | res_trafo | q_hv_mvar | float64
110 | res_trafo | p_lv_mw | float64
111 | res_trafo | q_lv_mvar | float64
112 | res_trafo | pl_mw | float64
113 | res_trafo | ql_mvar | float64
114 | res_trafo | i_hv_ka | float64
115 | res_trafo | i_lv_ka | float64
116 | res_trafo | vm_hv_pu | float64
117 | res_trafo | va_hv_degree | float64
118 | res_trafo | vm_lv_pu | float64
119 | res_trafo | va_lv_degree | float64
120 | res_trafo | loading_percent | float64
121 | res_ext_grid | p_mw | float64
122 | res_ext_grid | q_mvar | float64
123 | res_load | p_mw | float64
124 | res_load | q_mvar | float64
125 | res_shunt | p_mw | float64
126 | res_shunt | q_mvar | float64
127 | res_shunt | vm_pu | float64
128 | res_gen | p_mw | float64
129 | res_gen | q_mvar | float64
130 | res_gen | va_degree | float64
131 | res_gen | vm_pu | float64