## parameters
| version | converged | name | f_hz | sn_mva | OPF_converged
0 | 2.9.0 | TRUE | WACS | 50 | 1 | FALSE

## bus
| name | vn_kv | type | zone | in_service
0 | Ekibastuz | 500 | b |  | TRUE
1 | EGRES-1 | 500 | b |  | TRUE
2 | Nura | 500 | b |  | TRUE
3 | Agadyr | 500 | b |  | TRUE
4 | YkGRES | 500 | b |  | TRUE
5 | Almaty | 500 | b |  | TRUE
6 | Alma | 500 | b |  | TRUE
7 | Shu | 500 | b |  | TRUE
8 | Frunze | 500 | b |  | TRUE
9 | Zhambyl | 500 | b |  | TRUE
10 | Shymkent | 500 | b |  | TRUE
11 | Semey | 500 | b |  | TRUE
12 | Aktogay | 500 | b |  | TRUE
13 | Taldykorgan | 500 | b |  | TRUE
14 | Ust-Kamenogorsk | 500 | b |  | TRUE
15 | TashGRES | 500 | b |  | TRUE
16 | TsGPP | 500 | b |  | TRUE
17 | EEK | 500 | b |  | TRUE
18 | Rubtsovsk | 500 | b |  | TRUE
19 | Altai | 500 | b |  | TRUE
20 | U-K | 220 | b |  | TRUE
21 | Semey 220 | 220 | b |  | TRUE
22 | EEK 220 | 220 | b |  | TRUE
23 | EGRES-1 220 | 220 | b |  | TRUE
24 | TsGPP 220 | 220 | b |  | TRUE
25 | Osakarovka 220 | 220 | b |  | TRUE
26 | Nura 220 | 220 | b |  | TRUE
27 | Agadyr 220 | 220 | b |  | TRUE
28 | YkGRES 220 | 220 | b |  | TRUE
29 | Shu 220 | 220 | b |  | TRUE
30 | Glavnaya 220 | 220 | b |  | TRUE
31 | Taldykorgan 220 | 220 | b |  | TRUE
32 | Zapadnaya 220 | 220 | b |  | TRUE
33 | Kemin 220 | 220 | b |  | TRUE
34 | Frunze 220 | 220 | b |  | TRUE
35 | TashTES 220 | 220 | b |  | TRUE
36 | Barnaul | 500 | b |  | TRUE
37 | Kokshetau | 500 | b |  | TRUE
38 | Kostanay | 500 | b |  | TRUE
39 | Sokol | 500 | b |  | TRUE
40 | EGPP | 500 | b |  | TRUE
41 | Generatsia Sibiri | 500 | b |  | TRUE
42 | Troitskaya GRES | 510 | b |  | TRUE
43 | Zhezkazgan | 500 | b |  | TRUE
44 | Generatsia CA | 500 | b |  | TRUE
45 | EGRES 2 500 | 500 | b |  | TRUE
46 | Zhezkazgan 220 | 220 | b |  | TRUE
47 | KarGRES-2 | 220 | b |  | TRUE
48 | Mointy | 220 | b |  | TRUE
49 | Balhashskaya | 220 | b |  | TRUE
50 | EGRES-1 BL3-2 | 20 | b |  | TRUE
51 | Karazhal 220 | 220 | b |  | TRUE
52 | Tashkent | 500 | b |  | TRUE
53 | Avrora | 500 | b |  | TRUE
54 | Tavricheskaya | 500 | b |  | TRUE
55 | Irtyshskaya | 500 | b |  | TRUE
56 | pr/uz Semey-U-K | 220 | b |  | TRUE
57 | pr/uz EEK-Semey | 220 | b |  | TRUE
58 | pr/uz EGRES-1-EEK | 220 | b |  | TRUE
59 | pr/uz TsGPP-EGRES-1 | 220 | b |  | TRUE
60 | pr/uz TsGPP-Osakarovka | 220 | b |  | TRUE
61 | pr/uz EGRES-1-Osakarovka | 220 | b |  | TRUE
62 | pr/uz KarGRES-Nura | 220 | b |  | TRUE
63 | pr/uz KarGRES-Karazhal | 220 | b |  | TRUE
64 | pr/uz KarGRES-Agadyr | 220 | b |  | TRUE
65 | pr/uz KarGRES-Balhash | 220 | b |  | TRUE
66 | pr/uz YkGRES-Shu | 220 | b |  | TRUE
67 | pr/uz Almaty-Alma | 220 | b |  | TRUE
68 | pr/uz Glavnaya-Kemin | 220 | b |  | TRUE
69 | pr/uz Frunze-Kemin | 220 | b |  | TRUE
70 | pr/uz Zhambyl-Shymkent | 220 | b |  | TRUE
71 | pr/uz Glavnaya-Frunze | 220 | b |  | TRUE
72 | pr/uz Taldykorgan-Robot | 220 | b |  | TRUE
73 | pr/uz Mointy-YkGRES | 220 | b |  | TRUE
74 | pr/uz Zhezkazgan-Karazhal | 220 | b |  | TRUE
75 | Mirgalimsai | 220 | b |  | TRUE
76 | RU-6 | 220 | b |  | TRUE
77 | Kyzylorda 220 | 220 | b |  | TRUE
78 | Kumkol 220 | 220 | b |  | TRUE
79 | Medeo | 220 | b |  | TRUE
80 | Koyan-Kos | 220 | b |  | TRUE
81 | pr/uz Kyzylorda-Kumkol | 220 | b |  | TRUE
82 | Aspara | 220 | b |  | TRUE
83 | pr/uz ZhGRES-Frunze | 220 | b |  | TRUE
84 | Zhylga | 220 | b |  | TRUE
85 |  | 220 | b |  | TRUE
86 |  | 220 | b |  | TRUE
87 |  | 220 | b |  | TRUE
88 |  | 220 | b |  | TRUE
89 |  | 220 | b |  | TRUE
90 |  | 220 | b |  | TRUE
91 |  | 110 | b |  | TRUE
92 |  | 220 | b |  | TRUE
93 |  | 220 | b |  | TRUE
94 |  | 110 | b |  | TRUE
95 |  | 110 | b |  | TRUE
96 |  | 110 | b |  | TRUE
97 |  | 110 | b |  | TRUE
98 |  | 220 | b |  | TRUE
99 |  | 220 | b |  | TRUE
100 |  | 220 | b |  | TRUE
101 |  | 220 | b |  | TRUE
102 |  | 220 | b |  | TRUE
103 |  | 220 | b |  | TRUE
104 |  | 220 | b |  | TRUE
105 |  | 220 | b |  | TRUE
106 |  | 220 | b |  | TRUE
107 |  | 220 | b |  | TRUE
108 |  | 20 | b |  | TRUE
109 |  | 20 | b |  | TRUE
110 |  | 20 | b |  | TRUE
111 |  | 500 | b |  | TRUE
112 |  | 500 | b |  | TRUE
113 |  | 500 | b |  | TRUE
114 |  | 500 | b |  | TRUE
115 |  | 500 | b |  | TRUE
116 |  | 500 | b |  | TRUE
117 |  | 500 | b |  | TRUE
118 |  | 500 | b |  | TRUE
119 |  | 500 | b |  | TRUE
120 |  | 500 | b |  | TRUE
121 |  | 500 | b |  | TRUE
122 |  | 500 | b |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 |  | 3 | 10 | 0 | 0 | 0 |  | 1 | TRUE | wye
1 |  | 15 | 2500 | 0 | 0 | 0 |  | 1 | TRUE | wye
2 |  | 17 | 430 | 120 | 0 | 0 |  | 1 | TRUE | wye
3 |  | 18 | 175 | 79 | 0 | 0 |  | 1 | TRUE | wye
4 |  | 20 | 840 | 183 | 0 | 0 |  | 1 | TRUE | wye
5 |  | 21 | 180 | 50 | 0 | 0 |  | 1 | TRUE | wye
6 |  | 22 | 522.8 | 302 | 0 | 0 |  | 1 | TRUE | wye
7 |  | 23 | 360 | 50 | 0 | 0 |  | 1 | TRUE | wye
8 |  | 24 | 1050 | 98 | 0 | 0 |  | 1 | TRUE | wye
9 |  | 25 | 20.5 | 5.1 | 0 | 0 |  | 1 | TRUE | wye
10 |  | 26 | 67 | 20 | 0 | 0 |  | 1 | TRUE | wye
11 |  | 28 | 3 | 2 | 0 | 0 |  | 1 | TRUE | wye
12 |  | 29 | 12 | 2 | 0 | 0 |  | 1 | TRUE | wye
13 |  | 30 | 825 | 102 | 0 | 0 |  | 1 | TRUE | wye
14 |  | 31 | 202 | 27 | 0 | 0 |  | 1 | TRUE | wye
15 |  | 32 | 81.4 | 12.2 | 0 | 0 |  | 1 | TRUE | wye
16 |  | 33 | 420 | 76.2 | 0 | 0 |  | 1 | TRUE | wye
17 |  | 34 | 195 | 25 | 0 | 0 |  | 1 | TRUE | wye
18 |  | 35 | 660 | 70 | 0 | 0 |  | 1 | TRUE | wye
19 |  | 36 | 368 | 60 | 0 | 0 |  | 1 | TRUE | wye
20 |  | 37 | 255 | 60 | 0 | 0 |  | 1 | TRUE | wye
21 |  | 38 | 154 | 55 | 0 | 0 |  | 1 | TRUE | wye
22 |  | 39 | 304 | -25 | 0 | 0 |  | 1 | TRUE | wye
23 |  | 40 | 103.5 | -99.4 | 0 | 0 |  | 1 | TRUE | wye
24 |  | 41 | 2754 | 200 | 0 | 0 |  | 1 | TRUE | wye
25 |  | 42 | 280 | 66.7 | 0 | 0 |  | 1 | TRUE | wye
26 |  | 44 | 2295 | 25 | 0 | 0 |  | 1 | TRUE | wye
27 |  | 46 | 130 | 32 | 0 | 0 |  | 1 | TRUE | wye
28 |  | 48 | 6.4 | 2.1 | 0 | 0 |  | 1 | TRUE | wye
29 |  | 50 | 25 | 15 | 0 | 0 |  | 1 | TRUE | wye
30 |  | 51 | 33 | 3.2 | 0 | 0 |  | 1 | TRUE | wye
31 |  | 52 | 6964 | 3359 | 0 | 0 |  | 1 | FALSE | wye
32 |  | 53 | 232 | 10 | 0 | 0 |  | 1 | TRUE | wye
33 |  | 54 | 385 | 114 | 0 | 0 |  | 1 | TRUE | wye
34 |  | 55 | 174 | 11 | 0 | 0 |  | 1 | TRUE | wye
35 |  | 56 | 135 | 40 | 0 | 0 |  | 1 | TRUE | wye
36 |  | 57 | 24 | 9 | 0 | 0 |  | 1 | TRUE | wye
37 |  | 58 | 173 | 49.7 | 0 | 0 |  | 1 | TRUE | wye
38 |  | 59 | 38 | 18.8 | 0 | 0 |  | 1 | TRUE | wye
39 |  | 60 | 9.1 | 1.3 | 0 | 0 |  | 1 | TRUE | wye
40 |  | 61 | 54 | 30.4 | 0 | 0 |  | 1 | TRUE | wye
41 |  | 62 | 1183.4 | 452.2 | 0 | 0 |  | 1 | TRUE | wye
42 |  | 63 | 7.4 | 2.4 | 0 | 0 |  | 1 | TRUE | wye
43 |  | 64 | 20.3 | 7.9 | 0 | 0 |  | 1 | TRUE | wye
44 |  | 65 | 18 | 5.3 | 0 | 0 |  | 1 | TRUE | wye
45 |  | 66 | 15 | 4.6 | 0 | 0 |  | 1 | TRUE | wye
46 |  | 67 | 305 | 90 | 0 | 0 |  | 1 | TRUE | wye
47 |  | 68 | 320 | 15 | 0 | 0 |  | 1 | TRUE | wye
48 |  | 70 | 55.1 | 16.2 | 0 | 0 |  | 1 | TRUE | wye
49 |  | 71 | 175 | 30 | 0 | 0 |  | 1 | TRUE | wye
50 |  | 72 | 38.9 | 5 | 0 | 0 |  | 1 | TRUE | wye
51 |  | 73 | 13 | 4.2 | 0 | 0 |  | 1 | TRUE | wye
52 |  | 74 | 207 | 42.9 | 0 | 0 |  | 1 | TRUE | wye
53 |  | 52 | 30 | 9.1 | 0 | 0 |  | 1 | TRUE | wye
54 |  | 76 | 18 | 6 | 0 | 0 |  | 1 | TRUE | wye
55 |  | 77 | 154 | 44 | 0 | 0 |  | 1 | TRUE | wye
56 |  | 79 | 40 | 12 | 0 | 0 |  | 1 | TRUE | wye
57 |  | 80 | 12 | 2 | 0 | 0 |  | 1 | TRUE | wye
58 |  | 81 | 93 | -10 | 0 | 0 |  | 1 | TRUE | wye
59 |  | 82 | 8 | 2 | 0 | 0 |  | 1 | TRUE | wye
60 |  | 83 | 14 | 2 | 0 | 0 |  | 1 | TRUE | wye
61 |  | 84 | 11.3 | 4.5 | 0 | 0 |  | 1 | TRUE | wye
62 |  | 85 | 43 | 6.3 | 0 | 0 |  | 1 | TRUE | wye
63 |  | 86 | 18 | 3 | 0 | 0 |  | 1 | TRUE | wye
64 |  | 87 | 29.9 | 7.7 | 0 | 0 |  | 1 | TRUE | wye
65 |  | 88 | 20 | 3 | 0 | 0 |  | 1 | TRUE | wye
66 |  | 89 | 20 | 3.4 | 0 | 0 |  | 1 | TRUE | wye
67 |  | 90 | 24 | 19.3 | 0 | 0 |  | 1 | TRUE | wye
68 |  | 91 | 670 | 279 | 0 | 0 |  | 1 | TRUE | wye
69 |  | 92 | 50 | 15 | 0 | 0 |  | 1 | TRUE | wye
70 |  | 94 | 222 | 44.7 | 0 | 0 |  | 1 | TRUE | wye
71 |  | 95 | 80.6 | 35.1 | 0 | 0 |  | 1 | TRUE | wye
72 |  | 96 | 220 | 50 | 0 | 0 |  | 1 | TRUE | wye
73 |  | 97 | 394 | 152 | 0 | 0 |  | 1 | TRUE | wye
74 |  | 98 | 80 | 67.2 | 0 | 0 |  | 1 | TRUE | wye
75 |  | 100 | 55.7 | 14 | 0 | 0 |  | 1 | TRUE | wye
76 |  | 103 | 265 | 20 | 0 | 0 |  | 1 | TRUE | wye
77 |  | 104 | 322 | 88 | 0 | 0 |  | 1 | TRUE | wye
78 |  | 105 | 20 | 4 | 0 | 0 |  | 1 | TRUE | wye
79 |  | 106 | 386.3 | 59.8 | 0 | 0 |  | 1 | TRUE | wye
80 |  | 107 | 195.3 | 45.3 | 0 | 0 |  | 1 | TRUE | wye
81 |  | 108 | 12 | 3 | 0 | 0 |  | 1 | TRUE | wye
82 |  | 109 | 80 | 15 | 0 | 0 |  | 1 | TRUE | wye
83 |  | 110 | 22 | 8 | 0 | 0 |  | 1 | TRUE | wye
84 |  | 111 | 16 | 55 | 0 | 0 |  | 1 | TRUE | wye
85 |  | 112 | 140 | -35 | 0 | 0 |  | 1 | TRUE | wye
86 |  | 113 | -52.6 | 95 | 0 | 0 |  | 1 | TRUE | wye
87 |  | 114 | 716 | -196 | 0 | 0 |  | 1 | TRUE | wye
88 |  | 115 | -30 | 135 | 0 | 0 |  | 1 | TRUE | wye
89 |  | 116 | 256 | -33.8 | 0 | 0 |  | 1 | TRUE | wye
90 |  | 117 | 100000 | 40000 | 0 | 0 |  | 1 | TRUE | wye
91 |  | 118 | 584.8 | 40 | 0 | 0 |  | 1 | TRUE | wye
92 |  | 119 | 1 | 1 | 0 | 0 |  | 1 | TRUE | wye
93 |  | 120 | 178 | 40 | 0 | 0 |  | 1 | TRUE | wye
94 |  | 121 | 146.3 | -42.2 | 0 | 0 |  | 1 | TRUE | wye
95 |  | 122 | 5 | 165 | 0 | 0 |  | 1 | TRUE | wye

## gen
| name | bus | p_mw | vm_pu | sn_mva | min_q_mvar | max_q_mvar | scaling | slack | in_service | slack_weight | type | power_station_trafo
0 |  | 3 | 0 | 1.038 | 1000 | -360 |  | 1 | FALSE | TRUE | 0
1 |  | 4 | 0 | 1.042 | 1000 | -180 |  | 1 | FALSE | TRUE | 0
2 |  | 6 | 0 | 1.042 | 1000 | -180 |  | 1 | FALSE | TRUE | 0
3 |  | 8 | 0 | 1.02 | 1000 |  |  | 1 | FALSE | TRUE | 0
4 |  | 10 | 0 | 1.006 | 1000 |  |  | 1 | FALSE | TRUE | 0
5 |  | 11 | 0 | 1.02 | 1000 | -180 |  | 1 | FALSE | TRUE | 0
6 |  | 12 | 0 | 1.02 | 1000 | -180 |  | 1 | FALSE | TRUE | 0
7 |  | 13 | 0 | 1.02 | 1000 | -180 |  | 1 | FALSE | TRUE | 0
8 |  | 15 | 2934 | 1.02 | 4000 | -1000 | 1000 | 1 | FALSE | TRUE | 0
9 |  | 17 | 0 | 1.016 | 1000 | -180 |  | 1 | FALSE | TRUE | 0
10 |  | 20 | 1301 | 1.05 | 3000 | -383 | 896 | 1 | FALSE | TRUE | 0
11 |  | 21 | 10 | 1.077 | 1000 |  |  | 1 | FALSE | TRUE | 0
12 |  | 22 | 1120 | 1.07 | 1500 | -150 | 804 | 1 | FALSE | TRUE | 0
13 |  | 24 | 468 | 1.081 | 1000 | 40 | 250 | 1 | FALSE | TRUE | 0
14 |  | 26 | 0 | 1.05 | 1000 |  |  | 1 | FALSE | TRUE | 0
15 |  | 28 | 0 | 1 | 1000 |  |  | 1 | FALSE | TRUE | 0
16 |  | 29 | 0 | 1 | 1000 |  | 18 | 1 | FALSE | TRUE | 0
17 |  | 30 | 430 | 1.004 | 1000 | -100 | 100 | 1 | FALSE | TRUE | 0
18 |  | 31 | 36 | 1.045 | 1000 |  |  | 1 | FALSE | TRUE | 0
19 |  | 33 | 450.3 | 1.045 | 1000 | -160 | 300 | 1 | FALSE | TRUE | 0
20 |  | 35 | 776 | 1.045 | 1000 | -500 | 920 | 1 | FALSE | TRUE | 0
21 |  | 36 | 203 | 1.01 | 1000 |  |  | 1 | FALSE | TRUE | 0
22 |  | 41 | 3107 | 1.016 | 1000 | -1000 | 1000 | 1 | FALSE | TRUE | 0
23 |  | 42 | 46 | 0.99 | 1000 | -500 | 500 | 1 | FALSE | TRUE | 0
24 |  | 44 | 2520 | 1.02 | 4000 | -800 | 800 | 1 | FALSE | TRUE | 0
25 |  | 46 | 206 | 1.068 | 1000 | -25 | 232.5 | 1 | FALSE | TRUE | 0
26 |  | 48 | 0 | 1.045 | 1000 |  |  | 1 | FALSE | TRUE | 0
27 |  | 50 | 501 | 1 | 1000 | -130 | 340 | 1 | FALSE | TRUE | 0
28 |  | 52 | 7018 | 1.014 | 15000 | -2300 | 11500 | 1 | FALSE | FALSE | 0
29 |  | 53 | 250 | 1.01 | 1000 | -64 | 152 | 1 | FALSE | TRUE | 0
30 |  | 54 | 0 | 1.032 | 1000 | -180 |  | 1 | FALSE | TRUE | 0
31 |  | 62 | 946 | 1.059 | 2000 | 113.9 | 718.8 | 1 | FALSE | TRUE | 0
32 |  | 77 | 53 | 1 | 250 | -24 | 76 | 1 | FALSE | TRUE | 0
33 |  | 91 | 579 | 1.1 | 1000 | 92 | 437 | 1 | FALSE | TRUE | 0
34 |  | 93 | 78 | 1.11 | 1000 | -12 | 101 | 1 | FALSE | TRUE | 0
35 |  | 94 | 143 | 1.1 | 1000 | -30 | 88 | 1 | FALSE | TRUE | 0
36 |  | 95 | 96 | 1.1 | 1000 | -16.2 | 60.6 | 1 | FALSE | TRUE | 0
37 |  | 96 | 182 | 1.1 | 1000 | 20 | 160 | 1 | FALSE | TRUE | 0
38 |  | 97 | 577 | 1.1 | 1000 | 35 | 140 | 1 | FALSE | TRUE | 0
39 |  | 99 | 15 | 1.022 | 1000 | -10 | 10 | 1 | FALSE | TRUE | 0
40 |  | 100 | 177 | 1.072 | 1000 |  | 168 | 1 | FALSE | TRUE | 0
41 |  | 104 | 470 | 1.054 | 1000 | 120 | 422 | 1 | FALSE | TRUE | 0
42 |  | 106 | 127 | 1.077 | 1000 |  | 100 | 1 | FALSE | TRUE | 0
43 |  | 108 | 809 | 1 | 2000 | -163 | 573 | 1 | FALSE | TRUE | 0
44 |  | 109 | 2896 | 1 | 4000 | -430 | 1880 | 1 | FALSE | TRUE | 0
45 |  | 110 | 961 | 1 | 2000 | -500 | 800 | 1 | FALSE | TRUE | 0
46 |  | 115 | 550 | 1.02 | 1000 | -300 | 300 | 1 | FALSE | TRUE | 0
47 |  | 120 | 0 | 1.02 | 1000 | -180 |  | 1 | FALSE | TRUE | 0
48 |  | 121 | 0 | 1.034 | 1000 | -180 |  | 1 | FALSE | TRUE | 0
49 |  | 122 | 190 | 1 | 1000 |  |  | 1 | FALSE | TRUE | 0

## shunt
| bus | name | q_mvar | p_mw | vn_kv | step | max_step | in_service
0 | 0 |  | 1026 | 0 | 500 | 1 | 1 | TRUE
1 | 1 |  | 521 | 0 | 500 | 1 | 1 | TRUE
2 | 3 |  | 352 | 0 | 500 | 1 | 1 | TRUE
3 | 4 |  | 355 | 0 | 500 | 1 | 1 | TRUE
4 | 5 |  | 176 | 0 | 500 | 1 | 1 | TRUE
5 | 6 |  | 177 | 0 | 500 | 1 | 1 | TRUE
6 | 7 |  | 175 | 0 | 500 | 1 | 1 | TRUE
7 | 8 |  | 174 | 0 | 500 | 1 | 1 | TRUE
8 | 9 |  | 173 | 0 | 500 | 1 | 1 | TRUE
9 | 11 |  | 169 | 0 | 500 | 1 | 1 | TRUE
10 | 12 |  | 168 | 0 | 500 | 1 | 1 | TRUE
11 | 16 |  | 174 | 0 | 500 | 1 | 1 | TRUE
12 | 17 |  | 169 | 0 | 500 | 1 | 1 | TRUE
13 | 18 |  | 333 | 0 | 500 | 1 | 1 | TRUE
14 | 19 |  | 498 | 0 | 500 | 1 | 1 | TRUE
15 | 36 |  | 505 | 0 | 500 | 1 | 1 | TRUE
16 | 37 |  | 341 | 0 | 500 | 1 | 1 | TRUE
17 | 38 |  | 343 | 0 | 500 | 1 | 1 | TRUE
18 | 39 |  | 171 | 0 | 500 | 1 | 1 | TRUE
19 | 40 |  | 329 | 0 | 500 | 1 | 1 | TRUE
20 | 43 |  | 180 | 0 | 500 | 1 | 1 | TRUE
21 | 44 |  | 170 | 0 | 500 | 1 | 1 | TRUE
22 | 53 |  | 345 | 0 | 500 | 1 | 1 | TRUE
23 | 54 |  | 174 | 0 | 500 | 1 | 1 | TRUE
24 | 55 |  | 171 | 0 | 500 | 1 | 1 | TRUE
25 | 76 |  | 20 | 0 | 220 | 1 | 1 | TRUE
26 | 81 |  | 35 | 0 | 220 | 1 | 1 | TRUE
27 | 111 |  | 356 | 0 | 500 | 1 | 1 | TRUE
28 | 112 |  | 174 | 0 | 500 | 1 | 1 | TRUE
29 | 114 |  | 176 | 0 | 500 | 1 | 1 | TRUE
30 | 116 |  | 172 | 0 | 500 | 1 | 1 | TRUE
31 | 117 |  | 174 | 0 | 500 | 1 | 1 | TRUE
32 | 119 |  | 186 | 0 | 500 | 1 | 1 | TRUE
33 | 120 |  | 175 | 0 | 500 | 1 | 1 | TRUE
34 | 121 |  | 175 | 0 | 500 | 1 | 1 | TRUE
35 | 122 |  | 172 | 0 | 500 | 1 | 1 | TRUE

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 117 | 1.032 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 |  |  | 0 | 1 | 1 | 0.31 | 3.81 | 0.1531 | 0 | 10 | 1 | 1 | ol | TRUE
1 |  |  | 0 | 1 | 1 | 0.25 | 3.15 | 0.12636 | 0 | 10 | 1 | 1 | ol | TRUE
2 |  |  | 1 | 2 | 1 | 8.3 | 78.3 | 3.3423 | 0 | 10 | 1 | 1 | ol | TRUE
3 |  |  | 2 | 3 | 1 | 6.86 | 79.4 | 3.1862 | 0 | 10 | 1 | 1 | ol | TRUE
4 |  |  | 0 | 3 | 1 | 11.6 | 138.3 | 5.5939 | 0 | 10 | 1 | 1 | ol | TRUE
5 |  |  | 3 | 4 | 1 | 12.7 | 115.6 | 4.8574 | 0 | 10 | 1 | 1 | ol | TRUE
6 |  |  | 3 | 4 | 1 | 11.5 | 118.41 | 4.6065 | 0 | 10 | 1 | 1 | ol | TRUE
7 |  |  | 4 | 5 | 1 | 9.35 | 85 | 3.581 | 0 | 10 | 1 | 1 | ol | TRUE
8 |  |  | 4 | 6 | 1 | 9.2 | 98.2 | 3.6541 | 0 | 10 | 1 | 1 | ol | TRUE
9 |  |  | 4 | 7 | 1 | 5.2 | 63.6 | 2.5083 | 0 | 10 | 1 | 1 | ol | TRUE
10 |  |  | 5 | 7 | 1 | 7.1 | 72.41 | 2.8998 | 0 | 10 | 1 | 1 | ol | TRUE
11 |  |  | 5 | 6 | 1 | 1.8 | 19.5 | 0.72415 | 0 | 10 | 1 | 1 | ol | TRUE
12 |  |  | 7 | 8 | 1 | 2.82 | 28.85 | 1.1523 | 0 | 10 | 1 | 1 | ol | TRUE
13 |  |  | 8 | 9 | 1 | 6 | 69 | 2.5814 | 0 | 10 | 1 | 1 | ol | TRUE
14 |  |  | 9 | 10 | 1 | 4.1 | 51.6 | 1.948 | 0 | 10 | 1 | 1 | ol | TRUE
15 |  |  | 11 | 0 | 1 | 10.1 | 122.52 | 4.85 | 0 | 10 | 1 | 1 | ol | TRUE
16 |  |  | 11 | 12 | 1 | 9.84 | 120.42 | 4.53 | 0 | 10 | 1 | 1 | ol | TRUE
17 |  |  | 12 | 13 | 1 | 8.33 | 88.52 | 3.29 | 0 | 10 | 1 | 1 | ol | TRUE
18 |  |  | 13 | 6 | 1 | 5.91 | 62.76 | 2.33 | 0 | 10 | 1 | 1 | ol | TRUE
19 |  |  | 11 | 14 | 1 | 5.72 | 58.55 | 2.29 | 0 | 10 | 1 | 1 | ol | TRUE
20 |  |  | 15 | 10 | 1 | 3 | 32.5 | 1.44 | 0 | 10 | 1 | 1 | ol | TRUE
21 |  |  | 1 | 16 | 1 | 7.3 | 89.75 | 3.379 | 0 | 10 | 1 | 1 | ol | TRUE
22 |  |  | 1 | 17 | 1 | 3.05 | 36.64 | 1.473 | 0 | 10 | 1 | 1 | ol | TRUE
23 |  |  | 17 | 18 | 1 | 10.25 | 98.5 | 4.106 | 0 | 10 | 1 | 1 | ol | TRUE
24 |  |  | 18 | 14 | 1 | 4.34 | 44.02 | 1.782 | 0 | 10 | 1 | 1 | ol | TRUE
25 |  |  | 0 | 19 | 1 | 14.79 | 212.33 | 9.122 | 0 | 10 | 1 | 1 | ol | TRUE
26 |  |  | 29 | 30 | 1 | 16.8 | 72 | 1.496 | 0 | 10 | 1 | 1 | ol | TRUE
27 |  |  | 30 | 98 | 1 | 19 | 82 | 1.671 | 0 | 10 | 1 | 1 | ol | TRUE
28 |  |  | 32 | 33 | 1 | 9.27 | 40.58 | 0.794 | 0 | 10 | 1 | 1 | ol | TRUE
29 |  |  | 19 | 36 | 1 | 0.26 | 2.64 | 0.105 | 0 | 10 | 1 | 1 | ol | TRUE
30 |  |  | 36 | 18 | 1 | 10.3 | 105 | 4.364 | 0 | 10 | 1 | 1 | ol | TRUE
31 |  |  | 0 | 37 | 1 | 6.05 | 132.7 | 6.964 | 0 | 10 | 1 | 1 | ol | TRUE
32 |  |  | 37 | 38 | 1 | 5.02 | 106.96 | 5.56 | 0 | 10 | 1 | 1 | ol | TRUE
33 |  |  | 38 | 39 | 1 | 1.3 | 13.6 | 0.506 | 0 | 10 | 1 | 1 | ol | TRUE
34 |  |  | 16 | 40 | 1 | 11.12 | 113.36 | 4.548 | 0 | 10 | 1 | 1 | ol | TRUE
35 |  |  | 40 | 39 | 1 | 8.8 | 80 | 3.999 | 0 | 10 | 1 | 1 | ol | FALSE
36 |  |  | 39 | 116 | 1 | 4.7 | 53.5 | 2.126 | 0 | 10 | 1 | 1 | ol | TRUE
37 |  |  | 19 | 122 | 1 | 5.46 | 50.12 | 2.107 | 0 | 10 | 1 | 1 | ol | TRUE
38 |  |  | 3 | 43 | 1 | 12.6 | 123 | 4.889 | 0 | 10 | 1 | 1 | ol | TRUE
39 |  |  | 19 | 36 | 1 | 0.19 | 1.97 | 0.0786 | 0 | 10 | 1 | 1 | ol | TRUE
40 |  |  | 45 | 0 | 1 | 0.81 | 11.75 | 0.33 | 0 | 10 | 1 | 1 | ol | TRUE
41 |  |  | 45 | 0 | 1 | 0.93 | 11.27 | 0.312 | 0 | 10 | 1 | 1 | ol | TRUE
42 |  |  | 102 | 99 | 1 | 0.75 | 5.35 | 0.452 | 0 | 10 | 1 | 1 | ol | TRUE
43 |  |  | 101 | 80 | 1 | 0.57 | 3.15 | 0.257 | 0 | 10 | 1 | 1 | ol | TRUE
44 |  |  | 32 | 101 | 1 | 5 | 20 | 0.49 | 0 | 10 | 1 | 1 | ol | TRUE
45 |  |  | 99 | 100 | 1 | 2.1 | 14.2 | 0.298 | 0 | 10 | 1 | 1 | ol | TRUE
46 |  |  | 98 | 102 | 1 | 7 | 30.15 | 0.617 | 0 | 10 | 1 | 1 | ol | TRUE
47 |  |  | 27 | 49 | 1 | 23.67 | 99.68 | 2.037 | 0 | 10 | 1 | 1 | ol | TRUE
48 |  |  | 49 | 48 | 1 | 16.46 | 70.14 | 1.421 | 0 | 10 | 1 | 1 | ol | TRUE
49 |  |  | 48 | 27 | 1 | 12.8 | 54.2 | 1.113 | 0 | 10 | 1 | 1 | ol | TRUE
50 |  |  | 15 | 52 | 1 | 0.45 | 5.81 | 0.206 | 0 | 10 | 1 | 1 | ol | FALSE
51 |  |  | 37 | 53 | 1 | 5 | 49.9 | 1.951 | 0 | 10 | 1 | 1 | ol | TRUE
52 |  |  | 53 | 54 | 1 | 11.47 | 87.78 | 3.437 | 0 | 10 | 1 | 1 | ol | TRUE
53 |  |  | 1 | 54 | 1 | 11.8 | 108.2 | 4.583 | 0 | 10 | 1 | 1 | ol | TRUE
54 |  |  | 17 | 55 | 1 | 7.62 | 76.8 | 3.033 | 0 | 10 | 1 | 1 | ol | TRUE
55 |  |  | 54 | 55 | 1 | 3.42 | 35.28 | 1.394 | 0 | 10 | 1 | 1 | ol | TRUE
56 |  |  | 20 | 56 | 1 | 3.08 | 24.27 | 1.903 | 0 | 10 | 1 | 1 | ol | TRUE
57 |  |  | 21 | 56 | 1 | 3.08 | 24.27 | 1.903 | 0 | 10 | 1 | 1 | ol | TRUE
58 |  |  | 21 | 57 | 1 | 4.95 | 52.49 | 2.018 | 0 | 10 | 1 | 1 | ol | TRUE
59 |  |  | 22 | 57 | 1 | 4.94 | 52.48 | 2.018 | 0 | 10 | 1 | 1 | ol | TRUE
60 |  |  | 22 | 58 | 1 | 4.43 | 18.78 | 1.748 | 0 | 10 | 1 | 1 | ol | TRUE
61 |  |  | 23 | 58 | 1 | 4.43 | 18.78 | 1.748 | 0 | 10 | 1 | 1 | ol | TRUE
62 |  |  | 23 | 59 | 1 | 13.62 | 60.63 | 2.048 | 0 | 10 | 1 | 1 | ol | TRUE
63 |  |  | 24 | 59 | 1 | 13.62 | 60.63 | 2.048 | 0 | 10 | 1 | 1 | ol | TRUE
64 |  |  | 24 | 60 | 1 | 2.87 | 11.53 | 2.064 | 0 | 10 | 1 | 1 | ol | TRUE
65 |  |  | 25 | 60 | 1 | 2.86 | 11.52 | 2.064 | 0 | 10 | 1 | 1 | ol | TRUE
66 |  |  | 23 | 61 | 1 | 17.4 | 68.48 | 1.404 | 0 | 10 | 1 | 1 | ol | TRUE
67 |  |  | 25 | 61 | 1 | 17.4 | 68.48 | 1.404 | 0 | 10 | 1 | 1 | ol | TRUE
68 |  |  | 26 | 62 | 1 | 2.68 | 10.53 | 0.857 | 0 | 10 | 1 | 1 | ol | TRUE
69 |  |  | 47 | 62 | 1 | 2.68 | 10.52 | 0.857 | 0 | 10 | 1 | 1 | ol | TRUE
70 |  |  | 47 | 63 | 1 | 12.8 | 51.65 | 0.997 | 0 | 10 | 1 | 1 | ol | TRUE
71 |  |  | 51 | 63 | 1 | 12.8 | 51.65 | 0.997 | 0 | 10 | 1 | 1 | ol | TRUE
72 |  |  | 47 | 64 | 1 | 9.01 | 36.57 | 0.732 | 0 | 10 | 1 | 1 | ol | TRUE
73 |  |  | 27 | 64 | 1 | 9.01 | 36.56 | 0.732 | 0 | 10 | 1 | 1 | ol | TRUE
74 |  |  | 47 | 65 | 1 | 20.28 | 81.25 | 1.587 | 0 | 10 | 1 | 1 | ol | TRUE
75 |  |  | 49 | 65 | 1 | 20.28 | 81.25 | 1.587 | 0 | 10 | 1 | 1 | ol | TRUE
76 |  |  | 28 | 66 | 1 | 11.97 | 53.21 | 1.044 | 0 | 10 | 1 | 1 | ol | TRUE
77 |  |  | 29 | 66 | 1 | 11.97 | 53.21 | 1.044 | 0 | 10 | 1 | 1 | ol | TRUE
78 |  |  | 98 | 67 | 1 | 3.98 | 16.95 | 6.049 | 0 | 10 | 1 | 1 | ol | TRUE
79 |  |  | 99 | 67 | 1 | 3.98 | 16.95 | 6.049 | 0 | 10 | 1 | 1 | ol | TRUE
80 |  |  | 30 | 68 | 1 | 5.82 | 25.07 | 0.512 | 0 | 10 | 1 | 1 | ol | TRUE
81 |  |  | 33 | 68 | 1 | 5.82 | 25.07 | 0.512 | 0 | 10 | 1 | 1 | ol | TRUE
82 |  |  | 33 | 69 | 1 | 10.83 | 46.63 | 1.906 | 0 | 10 | 1 | 1 | ol | TRUE
83 |  |  | 34 | 69 | 1 | 10.83 | 46.63 | 1.906 | 0 | 10 | 1 | 1 | ol | TRUE
84 |  |  | 103 | 70 | 1 | 5.4 | 21.46 | 1.763 | 0 | 10 | 1 | 1 | ol | TRUE
85 |  |  | 106 | 70 | 1 | 5.4 | 21.46 | 1.763 | 0 | 10 | 1 | 1 | ol | TRUE
86 |  |  | 34 | 71 | 1 | 5.55 | 23.35 | 0.679 | 0 | 10 | 1 | 1 | ol | TRUE
87 |  |  | 30 | 71 | 1 | 5.55 | 23.35 | 0.679 | 0 | 10 | 1 | 1 | ol | TRUE
88 |  |  | 100 | 72 | 1 | 5 | 22.18 | 1.787 | 0 | 10 | 1 | 1 | ol | TRUE
89 |  |  | 31 | 72 | 1 | 5 | 22.18 | 1.787 | 0 | 10 | 1 | 1 | ol | TRUE
90 |  |  | 48 | 73 | 1 | 13.25 | 57.57 | 1.17 | 0 | 10 | 1 | 1 | ol | FALSE
91 |  |  | 28 | 73 | 1 | 13.24 | 57.56 | 1.17 | 0 | 10 | 1 | 1 | ol | TRUE
92 |  |  | 51 | 27 | 1 | 16.4 | 71.77 | 1.405 | 0 | 10 | 1 | 1 | ol | TRUE
93 |  |  | 51 | 74 | 1 | 7.68 | 29.92 | 2.744 | 0 | 10 | 1 | 1 | ol | TRUE
94 |  |  | 46 | 74 | 1 | 7.68 | 29.92 | 2.744 | 0 | 10 | 1 | 1 | ol | TRUE
95 |  |  | 98 | 100 | 1 | 7.71 | 33.81 | 0.662 | 0 | 10 | 1 | 1 | ol | TRUE
96 |  |  | 106 | 89 | 1 | 4.15 | 18.15 | 0.355 | 0 | 10 | 1 | 1 | ol | TRUE
97 |  |  | 105 | 76 | 1 | 21.97 | 85.81 | 1.807 | 0 | 10 | 1 | 1 | ol | TRUE
98 |  |  | 76 | 88 | 1 | 3.86 | 15.06 | 1.349 | 0 | 10 | 1 | 1 | ol | TRUE
99 |  |  | 77 | 81 | 1 | 27.39 | 107.65 | 2.289 | 0 | 10 | 1 | 1 | ol | TRUE
100 |  |  | 46 | 78 | 1 | 11.61 | 48.98 | 4.005 | 0 | 10 | 1 | 1 | ol | TRUE
101 |  |  | 79 | 102 | 1 | 0.33 | 1.49 | 0.029 | 0 | 10 | 1 | 1 | ol | TRUE
102 |  |  | 98 | 79 | 1 | 7.01 | 31.31 | 0.614 | 0 | 10 | 1 | 1 | ol | TRUE
103 |  |  | 80 | 102 | 1 | 0.43 | 2.38 | 0.194 | 0 | 10 | 1 | 1 | ol | TRUE
104 |  |  | 78 | 81 | 1 | 27.39 | 107.65 | 2.289 | 0 | 10 | 1 | 1 | ol | TRUE
105 |  |  | 103 | 104 | 1 | 1.45 | 5.71 | 1.034 | 0 | 10 | 1 | 1 | ol | TRUE
106 |  |  | 29 | 82 | 1 | 1.3 | 6 | 0.117 | 0 | 10 | 1 | 1 | ol | TRUE
107 |  |  | 82 | 104 | 1 | 21.9 | 86.36 | 1.818 | 0 | 10 | 1 | 1 | ol | TRUE
108 |  |  | 83 | 104 | 1 | 9.89 | 37.13 | 0.821 | 0 | 10 | 1 | 1 | ol | TRUE
109 |  |  | 83 | 34 | 1 | 9.89 | 37.13 | 0.821 | 0 | 10 | 1 | 1 | ol | TRUE
110 |  |  | 84 | 107 | 1 | 6.55 | 41.4 | 0.889 | 0 | 10 | 1 | 1 | ol | TRUE
111 |  |  | 84 | 87 | 1 | 9.98 | 39.67 | 0.827 | 0 | 10 | 1 | 1 | ol | TRUE
112 |  |  | 84 | 35 | 1 | 5.02 | 31.85 | 0.677 | 0 | 10 | 1 | 1 | ol | FALSE
113 |  |  | 35 | 107 | 1 | 8.58 | 52.04 | 1.149 | 0 | 10 | 1 | 1 | ol | TRUE
114 |  |  | 106 | 107 | 1 | 1.72 | 10.75 | 0.243 | 0 | 10 | 1 | 1 | ol | TRUE
115 |  |  | 75 | 107 | 1 | 19.7 | 79.3 | 1.509 | 0 | 10 | 1 | 1 | ol | TRUE
116 |  |  | 75 | 105 | 1 | 2.16 | 8.4 | 0.172 | 0 | 10 | 1 | 1 | ol | TRUE
117 |  |  | 105 | 85 | 1 | 13.39 | 52.29 | 1.555 | 0 | 10 | 1 | 1 | ol | TRUE
118 |  |  | 85 | 103 | 1 | 13.39 | 52.29 | 1.555 | 0 | 10 | 1 | 1 | ol | TRUE
119 |  |  | 8 | 44 | 1 | 7.1 | 64.2 | 2.584 | 0 | 10 | 1 | 1 | ol | TRUE
120 |  |  | 86 | 75 | 1 | 12.53 | 48.14 | 1.009 | 0 | 10 | 1 | 1 | ol | TRUE
121 |  |  | 86 | 76 | 1 | 7.21 | 28.31 | 0.591 | 0 | 10 | 1 | 1 | ol | TRUE
122 |  |  | 106 | 87 | 1 | 9.98 | 39.68 | 0.827 | 0 | 10 | 1 | 1 | ol | TRUE
123 |  |  | 77 | 88 | 1 | 3.86 | 15.06 | 1.349 | 0 | 10 | 1 | 1 | ol | TRUE
124 |  |  | 89 | 105 | 1 | 20.27 | 88.72 | 1.737 | 0 | 10 | 1 | 1 | ol | TRUE
125 |  |  | 25 | 90 | 1 | 8.88 | 38.87 | 0.761 | 0 | 10 | 1 | 1 | ol | TRUE
126 |  |  | 47 | 90 | 1 | 3.53 | 15.44 | 0.302 | 0 | 10 | 1 | 1 | ol | TRUE
127 |  |  | 99 | 92 | 1 | 12 | 52.7 | 1.031 | 0 | 10 | 1 | 1 | ol | TRUE
128 |  |  | 93 | 92 | 1 | 7.3 | 40.9 | 0.837 | 0 | 10 | 1 | 1 | ol | TRUE
129 |  |  | 93 | 100 | 1 | 17.1 | 95.7 | 1.957 | 0 | 10 | 1 | 1 | ol | TRUE
130 |  |  | 42 | 39 | 1 | 4.92 | 50 | 1.979 | 0 | 10 | 1 | 1 | ol | TRUE
131 |  |  | 117 | 116 | 1 | 5.05 | 57.9 | 2.304 | 0 | 10 | 1 | 1 | ol | TRUE
132 |  |  | 117 | 118 | 1 | 6.8 | 66 | 2.705 | 0 | 10 | 1 | 1 | ol | TRUE
133 |  |  | 118 | 42 | 1 | 6.2 | 54.6 | 2.435 | 0 | 10 | 1 | 1 | ol | TRUE
134 |  |  | 115 | 42 | 1 | 1.29 | 18.64 | 0.964 | 0 | 10 | 1 | 1 | ol | TRUE
135 |  |  | 113 | 115 | 1 | 1.78 | 25.87 | 1.278 | 0 | 10 | 1 | 1 | ol | TRUE
136 |  |  | 113 | 114 | 1 | 1.5 | 19 | 0.732 | 0 | 10 | 1 | 1 | ol | TRUE
137 |  |  | 38 | 114 | 1 | 4 | 75.3 | 4.52 | 0 | 10 | 1 | 1 | ol | TRUE
138 |  |  | 112 | 113 | 1 | 1.96 | 16.2 | 0.693 | 0 | 10 | 1 | 1 | ol | TRUE
139 |  |  | 112 | 111 | 1 | 9.02 | 84.65 | 3.393 | 0 | 10 | 1 | 1 | ol | TRUE
140 |  |  | 53 | 111 | 1 | 9.37 | 84.1 | 3.195 | 0 | 10 | 1 | 1 | ol | TRUE
141 |  |  | 111 | 119 | 1 | 9.4 | 87.42 | 3.546 | 0 | 10 | 1 | 1 | ol | TRUE
142 |  |  | 119 | 120 | 1 | 8.56 | 102.65 | 4.15 | 0 | 10 | 1 | 1 | ol | TRUE
143 |  |  | 120 | 54 | 1 | 2.1 | 21.85 | 0.87 | 0 | 10 | 1 | 1 | ol | TRUE
144 |  |  | 120 | 121 | 1 | 8.43 | 86.95 | 3.461 | 0 | 10 | 1 | 1 | ol | TRUE
145 |  |  | 122 | 121 | 1 | 10.8 | 110 | 4.376 | 0 | 10 | 1 | 1 | ol | TRUE
146 |  |  | 19 | 41 | 1 | 5 | 120 | 6.047 | 0 | 10 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service | pt_percent | oltc
0 |  |  | 14 | 20 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
1 |  |  | 14 | 20 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
2 |  |  | 11 | 21 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
3 |  |  | 17 | 22 | 801 | 500 | 220 | 11.9 | 0.17066 | 273.3 | 0.291 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
4 |  |  | 1 | 23 | 801 | 500 | 220 | 8.6 | 0.025121 | 297.45 | 0.15 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
5 |  |  | 16 | 24 | 501 | 500 | 220 | 11 | 0.14781 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
6 |  |  | 16 | 24 | 501 | 500 | 220 | 11 | 0.14781 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
7 |  |  | 2 | 26 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
8 |  |  | 3 | 27 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
9 |  |  | 4 | 28 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
10 |  |  | 7 | 29 | 501 | 500 | 220 | 9.5 | 0.031537 | 105 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
11 |  |  | 5 | 98 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
12 |  |  | 5 | 98 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
13 |  |  | 6 | 99 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
14 |  |  | 6 | 99 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
15 |  |  | 13 | 31 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
16 |  |  | 9 | 103 | 501 | 500 | 220 | 10.5 | 0.060413 | 206.49 | 0.35 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
17 |  |  | 8 | 34 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
18 |  |  | 8 | 34 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
19 |  |  | 15 | 35 | 501 | 500 | 220 | 11.5 | 0.20958 | 230 | 0.3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
20 |  |  | 10 | 106 | 501 | 500 | 220 | 11.8 | 0.072056 | 168.9 | 0.3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
21 |  |  | 10 | 106 | 501 | 500 | 220 | 11.8 | 0.072056 | 168.9 | 0.3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
22 |  |  | 45 | 110 | 630 | 500 | 20 | 14.7 | 0.20317 | 380 | 0.21 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
23 |  |  | 45 | 110 | 630 | 500 | 20 | 14.7 | 0.20317 | 380 | 0.21 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
24 |  |  | 1 | 109 | 630 | 500 | 20 | 14.2 | 0.20386 | 270.97 | 0.058 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
25 |  |  | 1 | 109 | 630 | 500 | 20 | 14 | 0.20635 | 460 | 0.35 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
26 |  |  | 1 | 109 | 630 | 500 | 20 | 14 | 0.20635 | 460 | 0.35 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
27 |  |  | 1 | 109 | 630 | 500 | 20 | 14 | 0.20635 | 460 | 0.35 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
28 |  |  | 1 | 109 | 630 | 500 | 20 | 14.2 | 0.24774 | 275.63 | 0.06 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
29 |  |  | 1 | 109 | 630 | 500 | 20 | 14.2 | 0.24774 | 275.63 | 0.06 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
30 |  |  | 43 | 46 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
31 |  |  | 23 | 50 | 630 | 242 | 20 | 12.5 | 0.20635 | 380 | 0.35 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
32 |  |  | 23 | 50 | 630 | 242 | 20 | 12.5 | 0.20635 | 380 | 0.35 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
33 |  |  | 17 | 108 | 400 | 525 | 20 | 12.6 | 0.20075 | 370 | 0.54 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
34 |  |  | 17 | 108 | 400 | 525 | 20 | 12.6 | 0.20125 | 385 | 0.35 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
35 |  |  | 17 | 108 | 400 | 525 | 20 | 14.8 | 0.19625 | 155 | 0.3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
36 |  |  | 17 | 108 | 400 | 525 | 20 | 14.8 | 0.19625 | 155 | 0.3 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
37 |  |  | 101 | 91 | 250 | 230 | 121 | 11 | 0.208 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
38 |  |  | 101 | 91 | 250 | 230 | 121 | 11 | 0.208 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
39 |  |  | 49 | 94 | 125 | 230 | 121 | 11 | 0.252 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
40 |  |  | 49 | 94 | 125 | 230 | 121 | 11 | 0.252 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
41 |  |  | 78 | 95 | 125 | 230 | 121 | 11 | 0.252 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
42 |  |  | 78 | 95 | 125 | 230 | 121 | 11 | 0.252 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
43 |  |  | 47 | 97 | 240 | 242 | 121 | 28.25 | 0.848 | 452 | 3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
44 |  |  | 47 | 97 | 240 | 242 | 121 | 28.25 | 0.848 | 452 | 3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
45 |  |  | 102 | 96 | 240 | 220 | 110 | 12.7 | 0.39583 | 450 | 3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9677 | -8.2274 | 0 | 960.7959
1 | 0.97388 | -7.9767 | 0 | 494.1367
2 | 0.99721 | -27.0254 | 0 | 0
3 | 1.038 | -39.2168 | 10 | -785.3385
4 | 1.042 | -55.851 | 0 | -715.3929
5 | 1.0215 | -61.6116 | 0 | 183.6616
6 | 1.042 | -60.563 | 0 | -633.341
7 | 1.0069 | -64.6616 | 0 | 177.4163
8 | 1.02 | -68.759 | 0 | -300.617
9 | 1.0045 | -72.6929 | 0 | 174.5467
10 | 1.006 | -73.509 | 0 | 639.6374
11 | 1.02 | -19.026 | 0 | -40.5615
12 | 1.02 | -39.5991 | 0 | -223.0533
13 | 1.02 | -54.1947 | 0 | 56.4273
14 | 1.0209 | -13.7225 | 0 | 0
15 | 1.02 | -70.4798 | -434 | 28.8648
16 | 1.0118 | -22.5178 | 0 | 178.1355
17 | 1.016 | -7.8202 | 430 | 192.969
18 | 0.97602 | -11.9692 | 175 | 396.219
19 | 1.0074 | -8.785 | 0 | 505.398
20 | 1.05 | -12.201 | -461 | -269.734
21 | 1.077 | -19.1158 | 170 | -385.861
22 | 1.07 | -5.6734 | -597.2 | -489.9638
23 | 1.0107 | -8.9195 | 360 | 50
24 | 1.081 | -25.8056 | 582 | -848.7169
25 | 1.0477 | -26.9864 | 20.5 | 5.1
26 | 1.05 | -30.6394 | 67 | -173.113
27 | 1.0372 | -39.6757 | 0 | 0
28 | 1 | -57.0087 | 3 | 190.1232
29 | 1 | -66.8769 | 12 | 60.663
30 | 1.004 | -83.9534 | 395 | -205.5945
31 | 1.045 | -57.3512 | 166 | -89.432
32 | 1.0204 | -72.7708 | 81.4 | 12.2
33 | 1.045 | -80.0417 | -30.3 | -161.9104
34 | 1.0181 | -72.2793 | 195 | 25
35 | 1.045 | -70.6186 | -116 | -94.6575
36 | 1.01 | -8.876 | 165 | -683.0478
37 | 0.93159 | -17.6357 | 255 | 355.9391
38 | 0.91408 | -18.7646 | 154 | 341.5879
39 | 0.92675 | -17.721 | 304 | 121.8669
40 | 0.91811 | -24.9254 | 103.5 | 177.9214
41 | 1.016 | 0.70688 | -353 | -32.443
42 | 0.99 | -17.0629 | 234 | 7.0379
43 | 1.0265 | -44.0697 | 0 | 189.6808
44 | 1.02 | -65.5463 | -225 | 18.6217
45 | 0.9729 | -6.9324 | 0 | 0
46 | 1.068 | -46.206 | -76 | -306.544
47 | 1.056 | -33.2995 | 0 | 0
48 | 1.045 | -41.192 | 6.4 | -14.7242
49 | 1.0374 | -42.3971 | 0 | 0
50 | 1 | -3.1092 | -476 | -426.3945
51 | 1.0148 | -44.4756 | 33 | 3.2
52 |  |  | 0 | 0
53 | 1.01 | -17.8723 | -18 | -600.745
54 | 1.032 | -16.8355 | 385 | -616.1069
55 | 1.0048 | -14.8724 | 174 | 183.6321
56 | 1.0474 | -17.3812 | 135 | 40
57 | 1.0603 | -13.0523 | 24 | 9
58 | 1.0223 | -8.9368 | 173 | 49.7
59 | 1.0175 | -18.8004 | 38 | 18.8
60 | 1.0639 | -26.4397 | 9.1 | 1.3
61 | 0.9842 | -19.9926 | 54 | 30.4
62 | 1.059 | -33.4784 | 237.4 | -124.997
63 | 1.0283 | -38.9724 | 7.4 | 2.4
64 | 1.0403 | -36.8248 | 20.3 | 7.9
65 | 1.0354 | -38.5504 | 18 | 5.3
66 | 0.99185 | -62.388 | 15 | 4.6
67 | 0.99044 | -66.2856 | 305 | 90
68 | 0.99742 | -86.5624 | 320 | 15
69 | 1.0292 | -76.2114 | 0 | 0
70 | 1.0488 | -76.3377 | 55.1 | 16.2
71 | 0.98747 | -80.4123 | 175 | 30
72 | 1.0548 | -59.9352 | 38.9 | 5
73 | 0.99128 | -57.8361 | 13 | 4.2
74 | 1.0102 | -48.6645 | 207 | 42.9
75 | 1.0158 | -81.6043 | 0 | 0
76 | 0.991 | -85.8983 | 18 | 25.6417
77 | 1 | -88.0385 | 101 | -92.0315
78 | 1.0238 | -54.6725 | 0 | 0
79 | 1.0291 | -65.226 | 40 | 12
80 | 1.0305 | -66.1576 | 12 | 2
81 | 0.91123 | -77.5259 | 93 | 19.062
82 | 1.0029 | -67.3891 | 8 | 2
83 | 1.0338 | -73.3319 | 14 | 2
84 | 1.0533 | -78.0864 | 11.3 | 4.5
85 | 1.0135 | -79.394 | 43 | 6.3
86 | 0.9966 | -84.6484 | 18 | 3
87 | 1.0591 | -77.9127 | 29.9 | 7.7
88 | 0.99405 | -87.1465 | 20 | 3
89 | 1.0637 | -77.6862 | 20 | 3.4
90 | 1.047 | -31.7485 | 24 | 19.3
91 | 1.1 | -68.5326 | 91 | -64.0616
92 | 1.0606 | -62.6856 | 50 | 15
93 | 1.11 | -60.4867 | -78 | -73.3659
94 | 1.1 | -44.4179 | 79 | -21.2003
95 | 1.1 | -54.3054 | -15.4 | -47.2036
96 | 1.1 | -66.3684 | 38 | -150.9031
97 | 1.1 | -26.9399 | -183 | -79.5307
98 | 1.0186 | -63.9937 | 80 | 67.2
99 | 1.022 | -62.9397 | -15 | 424.8299
100 | 1.072 | -61.5761 | -121.3 | -268.5262
101 | 1.0316 | -67.354 | 0 | 0
102 | 1.0302 | -65.2217 | 0 | 0
103 | 1.0336 | -74.8777 | 265 | 20
104 | 1.054 | -73.8052 | -148 | -207.6491
105 | 1.0156 | -81.4968 | 20 | 4
106 | 1.077 | -76.591 | 259.3 | -871.5884
107 | 1.0528 | -77.8255 | 195.3 | 45.3
108 | 1 | -2.6337 | -797 | -319.2463
109 | 1 | -1.8156 | -2816 | -811.0023
110 | 1 | -0.49583 | -939 | -273.1383
111 | 0.9209 | -18.4876 | 16 | 356.9062
112 | 0.95134 | -20.3219 | 140 | 122.4783
113 | 0.96668 | -20.1563 | -52.6 | 95
114 | 0.95395 | -22.6158 | 716 | -35.8355
115 | 1.02 | -17.0554 | -580 | -909.9699
116 | 0.94847 | -10.4417 | 256 | 120.929
117 | 1.032 | 0 | -1698.0585 | -570.6018
118 | 0.98363 | -13.2175 | 584.8 | 40
119 | 0.93363 | -17.7898 | 1 | 163.1292
120 | 1.02 | -17.3425 | 178 | -52.6889
121 | 1.034 | -15.6055 | 146.3 | -150.7264
122 | 1 | -9.4249 | -185 | 117.9921

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent | Ppanda | Qpanda | P_нач | Q_нач | Название
0 | -300.4384 | -367.1153 | 300.7364 | 370.7662 | 0.29798 | 3.6509 | 0.56605 | 0.56604 | 0.56605 | 0.9677 | -8.2274 | 0.97388 | -7.9767 | 5.6605 | 300.4384 | 367.1153 | 355.7438 | 8.1723 | ЭК-1150 - ЭГРЭС-1
1 | -362.5624 | -444.8247 | 362.914 | 449.2463 | 0.35167 | 4.4216 | 0.68476 | 0.68475 | 0.68476 | 0.9677 | -8.2274 | 0.97388 | -7.9767 | 6.8476 | 362.5624 | 444.8247 | 430.3441 | 8.2915 | ЭК-1150 - ЭГРЭС-1
2 | 1010.9546 | -10.0434 | -975.1751 | 347.3224 | 35.7795 | 337.279 | 1.1987 | 1.1987 | 1.1987 | 0.97388 | -7.9767 | 0.99721 | -27.0254 | 11.9872 | -1010.9546 | 10.0434 | -1009.0997 | 67.3387 | ЭГРЭС-1 - Нура
3 | 678.4815 | -113.3149 | -665.4256 | 264.1698 | 13.056 | 150.8549 | 0.79652 | 0.79644 | 0.79652 | 0.99721 | -27.0254 | 1.038 | -39.2168 | 7.9652 | -678.4815 | 113.3149 | -681.1073 | 169.9095 | Нура - Агадырь
4 | 939.71 | 57.1827 | -895.7924 | 465.9787 | 43.9176 | 523.1614 | 1.1234 | 1.1233 | 1.1234 | 0.9677 | -8.2274 | 1.038 | -39.2168 | 11.2337 | -939.71 | -57.1827 | -944.7787 | 87.75 | ЭК-1150 - Агадырь
5 | 671.2534 | 14.9564 | -649.9983 | 178.1027 | 21.2551 | 193.0591 | 0.74691 | 0.74685 | 0.74691 | 1.038 | -39.2168 | 1.042 | -55.851 | 7.4691 | -671.2534 | -14.9564 | -674.2982 | 189.8015 | Агадырь - ЮКГРЭС
6 | 655.9403 | 22.8971 | -637.5483 | 166.0855 | 18.392 | 188.9826 | 0.73013 | 0.73008 | 0.73013 | 1.038 | -39.2168 | 1.042 | -55.851 | 7.3013 | -655.9403 | -22.8971 | -658.9096 | 171.2337 | Агадырь - ЮКГРЭС
7 | 319.0165 | 43.2878 | -315.4459 | -11.1272 | 3.5706 | 32.1606 | 0.35676 | 0.35679 | 0.35679 | 1.042 | -55.851 | 1.0215 | -61.6116 | 3.5679 | -319.0165 | -43.2878 | -294.0276 | 156.4373 | ЮКГРЭС - Алматы
8 | 225.9626 | -11.9829 | -224.2273 | 30.1937 | 1.7353 | 18.2108 | 0.25075 | 0.25072 | 0.25075 | 1.042 | -55.851 | 1.042 | -60.563 | 2.5075 | -225.9626 | 11.9829 | -191.6675 | 167.0373 | ЮКГРЭС - Алма
9 | 643.1202 | 139.8232 | -634.8217 | -38.5328 | 8.2985 | 101.2904 | 0.72933 | 0.72936 | 0.72936 | 1.042 | -55.851 | 1.0069 | -64.6616 | 7.2936 | -643.1202 | -139.8232 | -684.0527 | 61.7092 | ЮКГРЭС - ЧУ
10 | 192.6524 | 37.7051 | -191.6034 | -27.2408 | 1.049 | 10.4643 | 0.2219 | 0.22194 | 0.22194 | 1.0215 | -61.6116 | 1.0069 | -64.6616 | 2.2194 | -192.6524 | -37.7051 | -255.4242 | 115.9621 | Алматы - ЧУ
11 | -271.9557 | -240.6736 | 272.8655 | 250.4697 | 0.90985 | 9.7962 | 0.4105 | 0.41045 | 0.4105 | 1.0215 | -61.6116 | 1.042 | -60.563 | 4.105 | 271.9557 | 240.6736 | 321.4078 | 62.0089 | Алматы - Алма
12 | 620.9994 | -152.4735 | -616.4501 | 198.9221 | 4.5493 | 46.4486 | 0.73332 | 0.73329 | 0.73332 | 1.0069 | -64.6616 | 1.02 | -68.759 | 7.3332 | -620.9994 | 152.4735 | -701.9235 | 51.0808 | ЧУ - Фрунзе
13 | 258.477 | 43.5941 | -256.8917 | -25.5716 | 1.5852 | 18.0225 | 0.29674 | 0.29678 | 0.29678 | 1.02 | -68.759 | 1.0045 | -72.6929 | 2.9678 | -258.477 | -43.5941 | -259.3142 | 116.0323 | Фрунзе - Жамбыл
14 | 68.7375 | -12.5353 | -68.6582 | 13.379 | 0.079324 | 0.84372 | 0.080322 | 0.080289 | 0.080322 | 1.0045 | -72.6929 | 1.006 | -73.509 | 0.80322 | -68.7375 | 12.5353 | -68.4377 | 67.6198 | Жамбыл - Шымкент
15 | -362.973 | 174.2358 | 369.2705 | -98.2191 | 6.2975 | 76.0167 | 0.4558 | 0.45595 | 0.45595 | 1.02 | -19.026 | 0.9677 | -8.2274 | 4.5595 | 362.973 | -174.2358 | 300.5696 | 175.0602 | Семей - ЭК-1150
16 | 765.1535 | 75.0417 | -742.7905 | 198.2619 | 22.363 | 273.3036 | 0.87035 | 0.87032 | 0.87035 | 1.02 | -19.026 | 1.02 | -39.5991 | 8.7035 | -765.1535 | -75.0417 | -764.8434 | 100.4579 | Семей - Актогай
17 | 742.7905 | 24.7914 | -725.1006 | 162.9244 | 17.6899 | 187.7159 | 0.84135 | 0.84132 | 0.84135 | 1.02 | -39.5991 | 1.02 | -54.1947 | 8.4135 | -742.7905 | -24.7914 | -742.3606 | 175.7766 | Актогай - Талдыкорган
18 | 459.5711 | -106.6357 | -454.5142 | 160.1422 | 5.0569 | 53.5065 | 0.53408 | 0.53402 | 0.53408 | 1.02 | -54.1947 | 1.042 | -60.563 | 5.3408 | -459.5711 | 106.6357 | -462.0292 | 133.649 | Талдыкорган - Алма
19 | -405.6184 | 54.7085 | 409.3026 | -17.1839 | 3.6842 | 37.5246 | 0.46334 | 0.46336 | 0.46336 | 1.02 | -19.026 | 1.0209 | -13.7225 | 4.6336 | 405.6184 | -54.7085 | 408.2937 | -5.329 | Семей - Усть-Каменогорск
20 | 424.6554 | 81.6173 | -422.4985 | -58.3669 | 2.1569 | 23.2503 | 0.48953 | 0.48956 | 0.48956 | 1.02 | -70.4798 | 1.006 | -73.509 | 4.8956 | -424.6554 | -81.6173 | -358.6374 | 97.1823 | Таш.ГРЭС - Шымкент
21 | 683.4118 | -70.6993 | -668.8792 | 249.1097 | 14.5327 | 178.4104 | 0.81463 | 0.81456 | 0.81463 | 0.97388 | -7.9767 | 1.0118 | -22.5178 | 8.1463 | -683.4118 | 70.6993 | -653.2797 | 122.5359 | ЭГРЭС-1 - ЦГПП
22 | -41.4514 | -276.474 | 42.4563 | 288.432 | 1.005 | 11.958 | 0.33147 | 0.33134 | 0.33147 | 0.97388 | -7.9767 | 1.016 | -7.8202 | 3.3147 | 41.4514 | 276.474 | 102.1757 | -43.4848 | ЭГРЭС-1 - ЕЭК
23 | 191.4376 | 89.6111 | -189.6618 | -72.8665 | 1.7758 | 16.7446 | 0.24023 | 0.24037 | 0.24037 | 1.016 | -7.8202 | 0.97602 | -11.9692 | 2.4037 | -191.4376 | -89.6111 | -142.5615 | 160.07 | ЕЭК - Рубцовск
24 | 147.4434 | -260.6631 | -145.8097 | 277.0944 | 1.6337 | 16.4313 | 0.3543 | 0.35416 | 0.3543 | 0.97602 | -11.9692 | 1.0209 | -13.7225 | 3.543 | -147.4434 | 260.6631 | -72.4976 | 74.9363 | Рубцовск - Усть-Каменогорск
25 | 7.9856 | -46.0684 | -7.8494 | 47.3241 | 0.13616 | 1.2557 | 0.05579 | 0.054985 | 0.05579 | 0.9677 | -8.2274 | 1.0074 | -8.785 | 0.5579 | -7.9856 | 46.0684 | 11.8602 | 362.0922 | ЭК-1150 - Алтай
26 | 193.9424 | -18.1991 | -180.7716 | 74.6226 | 13.1708 | 56.4235 | 0.5112 | 0.51119 | 0.5112 | 1 | -66.8769 | 1.004 | -83.9534 | 5.112 | -193.9424 | 18.1991 | -228.7083 | -45.2824 | Шу 220 - Главная 220
27 | -189.4681 | 71.5215 | 205.4411 | -2.6113 | 15.973 | 68.9102 | 0.52935 | 0.52937 | 0.52937 | 1.004 | -83.9534 | 1.0186 | -63.9937 | 5.2937 | 189.4681 | -71.5215 | 225.3336 | -27.2484 | Главная 220 - Алматы 220
28 | 148.716 | -53.6381 | -144.119 | 73.7487 | 4.597 | 20.1106 | 0.40658 | 0.40656 | 0.40658 | 1.0204 | -72.7708 | 1.045 | -80.0417 | 4.0658 | -148.716 | 53.6381 | -474.8556 | 38.2318 | Западная 220 - Кемин 220
29 | 127.4194 | -260.4357 | -127.3333 | 261.302 | 0.086143 | 0.86629 | 0.33233 | 0.33232 | 0.33233 | 1.0074 | -8.785 | 1.01 | -8.876 | 3.3233 | -127.4194 | 260.4357 | -116.021 | -98.7912 | Алтай - Барнаул
30 | 133.7132 | 71.8484 | -132.7816 | -62.6894 | 0.93162 | 9.159 | 0.17354 | 0.17372 | 0.17372 | 1.01 | -8.876 | 0.97602 | -11.9692 | 1.7372 | -133.7132 | -71.8484 | -106.1961 | 172.7436 | Барнаул - Рубцовск
31 | 281.0926 | 75.6146 | -278.9019 | -28.0588 | 2.1906 | 47.5558 | 0.34733 | 0.34744 | 0.34744 | 0.9677 | -8.2274 | 0.93159 | -17.6357 | 3.4744 | -281.0926 | -75.6146 | -486.5922 | 240.9824 | ЭК-1150 - Кокшетау
32 | 40.9308 | 36.4092 | -40.861 | -35.2949 | 0.069755 | 1.1143 | 0.067901 | 0.068208 | 0.068208 | 0.93159 | -17.6357 | 0.91408 | -18.7646 | 0.68208 | -40.9308 | -36.4092 | -542.1603 | 189.5116 | Кокшетау - Костанай
33 | -300.9757 | -181.6845 | 301.7449 | 189.6975 | 0.76917 | 8.013 | 0.44411 | 0.44409 | 0.44411 | 0.91408 | -18.7646 | 0.92675 | -17.721 | 4.4411 | 300.9757 | 181.6845 | -569.7917 | 40.3751 | Костанай - Сокол
34 | 105.7329 | 200.3507 | -103.5 | -177.9214 | 2.2329 | 22.4293 | 0.25853 | 0.25888 | 0.25888 | 1.0118 | -22.5178 | 0.91811 | -24.9254 | 2.5888 | -105.7329 | -200.3507 | -104.0813 | 134.4992 | ЦГПП - ПС-ЕГПП
35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91811 | -24.9254 | 0.92675 | -17.721 | 0 | 0 | 0 | 0 | 0 | ПС-ЕГПП - Сокол
36 | -521.7656 | -15.1604 | 527.7297 | 82.9027 | 5.9641 | 67.7423 | 0.65038 | 0.65036 | 0.65038 | 0.92675 | -17.721 | 0.94847 | -10.4417 | 6.5038 | 521.7656 | 15.1604 | -482.9138 | 127.4349 | Сокол - Житикара
37 | 59.502 | 30.9335 | -59.4051 | -30.2108 | 0.096897 | 0.72275 | 0.076868 | 0.076956 | 0.076956 | 1.0074 | -8.785 | 1 | -9.4249 | 0.76956 | -59.502 | -30.9335 | -67.4436 | 143.3129 | Алтай - Заря
38 | 184.5527 | 12.8313 | -182.9515 | 2.39 | 1.6012 | 15.2213 | 0.2058 | 0.20581 | 0.20581 | 1.038 | -39.2168 | 1.0265 | -44.0697 | 2.0581 | -184.5527 | -12.8313 | -186.5321 | 242.2039 | Агадырь - ЖЕЗКАЗГАН
39 | 171.493 | -348.731 | -171.3799 | 349.8973 | 0.1131 | 1.1663 | 0.44544 | 0.44543 | 0.44544 | 1.0074 | -8.785 | 1.01 | -8.876 | 4.4544 | -171.493 | 348.731 | -155.2313 | -135.2662 | Алтай - Барнаул
40 | 458.2968 | 81.1745 | -457.5552 | -70.4424 | 0.74151 | 10.7321 | 0.5524 | 0.55241 | 0.55241 | 0.9729 | -6.9324 | 0.9677 | -8.2274 | 5.5241 | -458.2968 | -81.1745 | -459.5197 | -51.7355 | ЭГРЕС-2 500 - ЭК-1150
41 | 478.4261 | 78.092 | -477.5026 | -66.9234 | 0.92354 | 11.1686 | 0.57534 | 0.57534 | 0.57534 | 0.9729 | -6.9324 | 0.9677 | -8.2274 | 5.7534 | -478.4261 | -78.092 | -479.4803 | -48.7104 | ЭГРЕС-2 500 - ЭК-1150
42 | -360.3771 | 134.8997 | 362.5389 | -119.4864 | 2.1617 | 15.4132 | 0.98019 | 0.9802 | 0.9802 | 1.0302 | -65.2217 | 1.022 | -62.9397 | 9.802 | 360.3771 | -134.8997 | 261.1784 | 50.4494 | АТЭЦ-3 - Алма 220
43 | -326.719 | 79.144 | 327.9697 | -72.2364 | 1.2507 | 6.9076 | 0.85522 | 0.85522 | 0.85522 | 1.0316 | -67.354 | 1.0305 | -66.1576 | 8.5522 | 326.719 | -79.144 | 173.0754 | 84.8247 | ПС-7 АХБК - Коян-Кос
44 | -230.116 | 41.4381 | 235.5397 | -19.7508 | 5.4238 | 21.6873 | 0.60132 | 0.60132 | 0.60132 | 1.0204 | -72.7708 | 1.0316 | -67.354 | 6.0132 | 230.116 | -41.4381 | 81.3996 | 12.2 | Западная 220 - ПС-7 АХБК
45 | -112.0134 | -156.5514 | 113.5526 | 166.9548 | 1.5393 | 10.4034 | 0.4943 | 0.49429 | 0.4943 | 1.022 | -62.9397 | 1.072 | -61.5761 | 4.943 | 112.0134 | 156.5514 | 105.0533 | 46.1519 | Алма 220 - Робот
46 | 30.1285 | -25.7307 | -29.9097 | 26.6633 | 0.21881 | 0.93259 | 0.10208 | 0.10207 | 0.10208 | 1.0186 | -63.9937 | 1.0302 | -65.2217 | 1.0208 | -30.1285 | 25.7307 | -0.5892 | -18.5106 | Алматы 220 - АТЭЦ-3
47 | 23.597 | -5.1114 | -23.3321 | 6.1936 | 0.2649 | 1.0822 | 0.061087 | 0.061067 | 0.061087 | 1.0372 | -39.6757 | 1.0374 | -42.3971 | 0.61087 | -23.597 | 5.1114 | -23.618 | 23.5728 | Агадырь 220 - Балхашская
48 | -16.0834 | -1.5053 | 16.1659 | 1.8332 | 0.082446 | 0.3279 | 0.040864 | 0.040858 | 0.040864 | 1.0374 | -42.3971 | 1.045 | -41.192 | 0.40864 | 16.0834 | 1.5053 | 16.144 | 15.0012 | Балхашская - Мойынты
49 | -22.5659 | 12.8911 | 22.7295 | -12.2166 | 0.16362 | 0.6745 | 0.065265 | 0.065287 | 0.065287 | 1.045 | -41.192 | 1.0372 | -39.6757 | 0.65287 | 22.5659 | -12.8911 | 22.6251 | -7.0837 | Мойынты - Агадырь 220
50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1.02 | -70.4798 |  |  |  | 0 | 0 | 0 | 0 | Таш.ГРЭС - Ташкент
51 | -17.0288 | -364.2895 | 20.0927 | 394.7219 | 3.0638 | 30.4324 | 0.45203 | 0.45186 | 0.45203 | 0.93159 | -17.6357 | 1.01 | -17.8723 | 4.5203 | 17.0288 | 364.2895 | 316.0282 | -10.476 | Кокшетау - АВРОРА 500
52 | -60.8792 | -54.98 | 61.1811 | 57.0095 | 0.30197 | 2.0295 | 0.093783 | 0.093568 | 0.093783 | 1.01 | -17.8723 | 1.032 | -16.8355 | 0.93783 | 60.8792 | 54.98 | 135.7654 | 139.6293 | АВРОРА 500 - ТАВРИЧЕСКАЯ
53 | 342.3064 | -140.5839 | -335.494 | 202.6881 | 6.8124 | 62.1043 | 0.43876 | 0.43857 | 0.43876 | 0.97388 | -7.9767 | 1.032 | -16.8355 | 4.3876 | -342.3064 | 140.5839 | -347.2406 | 184.317 | ЭГРЭС-1 - ТАВРИЧЕСКАЯ
54 | 410.1303 | 21.4959 | -405.1498 | 28.4584 | 4.9805 | 49.9544 | 0.46676 | 0.46676 | 0.46676 | 1.016 | -7.8202 | 1.0048 | -14.8724 | 4.6676 | -410.1303 | -21.4959 | -418.2038 | 135.1259 | ЕЭК - ИРТЫШСКАЯ
55 | -229.8165 | 225.7303 | 231.1498 | -212.0905 | 1.3332 | 13.6398 | 0.36043 | 0.36052 | 0.36052 | 1.032 | -16.8355 | 1.0048 | -14.8724 | 3.6052 | 229.8165 | -225.7303 | 238.2275 | -15.3538 | ТАВРИЧЕСКАЯ - ИРТЫШСКАЯ
56 | 196.6774 | -10.6588 | -194.4382 | 28.2721 | 2.2393 | 17.6133 | 0.49229 | 0.49228 | 0.49229 | 1.05 | -12.201 | 1.0474 | -17.3812 | 4.9229 | -196.6774 | 10.6588 | -121.2192 | 33.9699 | У-К - пр/уз. Семей У-К
57 | -58.963 | 71.9835 | 59.4382 | -68.2721 | 0.47514 | 3.7114 | 0.22673 | 0.2268 | 0.2268 | 1.077 | -19.1158 | 1.0474 | -17.3812 | 2.268 | 58.963 | -71.9835 | 136.9914 | -61.6411 | Семей 220 - пр/уз. Семей У-К
58 | -108.1504 | 32.6308 | 109.2756 | -20.7333 | 1.1253 | 11.8975 | 0.27526 | 0.27528 | 0.27528 | 1.077 | -19.1158 | 1.0603 | -13.0523 | 2.7528 | 108.1504 | -32.6308 | 88.9887 | 9.8837 | Семей 220 - пр/уз. ЕЭК Семей
59 | 134.9007 | 5.4956 | -133.2756 | 11.7333 | 1.6251 | 17.2289 | 0.33114 | 0.33113 | 0.33114 | 1.07 | -5.6734 | 1.0603 | -13.0523 | 3.3114 | -134.9007 | -5.4956 | -114.8794 | 32.5678 | ПС-ЕЭК 220 - пр/уз. ЕЭК Семей
60 | 182.4402 | 93.0877 | -179.0863 | -78.8987 | 3.3539 | 14.189 | 0.50234 | 0.50237 | 0.50237 | 1.07 | -5.6734 | 1.0223 | -8.9368 | 5.0237 | -182.4402 | -93.0877 | -186.133 | -7.7358 | ПС-ЕЭК 220 - пр/уз. Эгрэс-1 ЕЭК
61 | -6.0083 | -28.8956 | 6.0863 | 29.1987 | 0.077984 | 0.30313 | 0.076637 | 0.076567 | 0.076637 | 1.0107 | -8.9195 | 1.0223 | -8.9368 | 0.76637 | 6.0083 | 28.8956 | 22.2938 | 14.2504 | ЭГРЭС-1 220 - пр/уз. Эгрэс-1 ЕЭК
62 | 135.5263 | -23.7967 | -130.3103 | 46.9842 | 5.2161 | 23.1875 | 0.3573 | 0.35728 | 0.3573 | 1.0107 | -8.9195 | 1.0175 | -18.8004 | 3.573 | -135.5263 | 23.7967 | -122.624 | 47.8782 | ЭГРЭС-1 220 - пр/уз.ЦГПП-ЭГРЭС-1
63 | -88.8184 | 81.2942 | 92.3103 | -65.7842 | 3.4919 | 15.51 | 0.29231 | 0.29236 | 0.29236 | 1.081 | -25.8056 | 1.0175 | -18.8004 | 2.9236 | 88.8184 | -81.2942 | 107.2339 | -28.9769 | ПС-ЦГПП 220 - пр/уз.ЦГПП-ЭГРЭС-1
64 | 68.5617 | 60.7633 | -68.1357 | -59.088 | 0.426 | 1.6753 | 0.22241 | 0.22246 | 0.22246 | 1.081 | -25.8056 | 1.0639 | -26.4397 | 2.2246 | -68.5617 | -60.7633 | -62.2776 | 31.836 | ПС-ЦГПП 220 - пр/уз.ЦГПП-Осакоровка
65 | -58.6794 | -56.3874 | 59.0357 | 57.788 | 0.35639 | 1.4005 | 0.20384 | 0.20378 | 0.20384 | 1.0477 | -26.9864 | 1.0639 | -26.4397 | 2.0384 | 58.6794 | 56.3874 | 52.8078 | 38.5659 | Оскаровка 220 - пр/уз.ЦГПП-Осакоровка
66 | 134.4699 | -2.1892 | -128.104 | 27.2219 | 6.3659 | 25.0327 | 0.34922 | 0.34921 | 0.34922 | 1.0107 | -8.9195 | 0.9842 | -19.9926 | 3.4922 | -134.4699 | 2.1892 | -137.814 | 23.1594 | ЭГРЭС-1 220 - пр/уз.ЭГРЭС 1 Осакоровка
67 | -70.8341 | 70.4691 | 74.104 | -57.6219 | 3.2699 | 12.8472 | 0.25026 | 0.2503 | 0.2503 | 1.0477 | -26.9864 | 0.9842 | -19.9926 | 2.503 | 70.8341 | -70.4691 | 74.9063 | -41.7341 | Оскаровка 220 - пр/уз.ЭГРЭС 1 Осакоровка
68 | 228.8671 | -95.419 | -225.7792 | 107.5374 | 3.0879 | 12.1184 | 0.61974 | 0.61973 | 0.61974 | 1.05 | -30.6394 | 1.059 | -33.4784 | 6.1974 | -228.8671 | 95.419 | -224.7964 | 102.2603 | Нура 220 - пр/уз.КарГРЭС-Нура
69 | 11.6426 | -17.3889 | -11.6208 | 17.4596 | 0.021731 | 0.07073 | 0.052004 | 0.051974 | 0.052004 | 1.056 | -33.2995 | 1.059 | -33.4784 | 0.52004 | -11.6426 | 17.3889 | -11.7291 | 3.0077 | Кар.ГРЭС-2 - пр/уз.КарГРЭС-Нура
70 | 102.3371 | 7.0437 | -99.8417 | 3.0091 | 2.4954 | 10.0528 | 0.25492 | 0.25492 | 0.25492 | 1.056 | -33.2995 | 1.0283 | -38.9724 | 2.5492 | -102.3371 | -7.0437 | -104.4833 | 37.5231 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Каражал
71 | -90.2972 | 14.0469 | 92.4417 | -5.4091 | 2.1445 | 8.6377 | 0.23632 | 0.23632 | 0.23632 | 1.0148 | -44.4756 | 1.0283 | -38.9724 | 2.3632 | 90.2972 | -14.0469 | 92.1041 | -25.3106 | Каражал 220 - пр/уз.Каргрэс-Каражал
72 | 90.0289 | 2.5206 | -88.6749 | 2.963 | 1.3541 | 5.4836 | 0.22382 | 0.22382 | 0.22382 | 1.056 | -33.2995 | 1.0403 | -36.8248 | 2.2382 | -90.0289 | -2.5206 | -87.9493 | 20.9686 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Агадырь
73 | -67.5504 | 14.1963 | 68.3749 | -10.863 | 0.82443 | 3.3333 | 0.17464 | 0.17465 | 0.17465 | 1.0372 | -39.6757 | 1.0403 | -36.8248 | 1.7465 | 67.5504 | -14.1963 | 65.5625 | -12.3795 | Агадырь 220 - пр/уз.Каргрэс-Агадырь
74 | 59.8027 | 0.75885 | -58.4587 | 4.5992 | 1.344 | 5.3581 | 0.14863 | 0.14862 | 0.14863 | 1.056 | -33.2995 | 1.0354 | -38.5504 | 1.4863 | -59.8027 | -0.75885 | -59.6022 | 32.1291 | Кар.ГРЭС-2 - пр/уз.Каргрэс - Балхашская
75 | -39.7808 | 12.5895 | 40.4587 | -9.8992 | 0.67796 | 2.6903 | 0.10555 | 0.10557 | 0.10557 | 1.0374 | -42.3971 | 1.0354 | -38.5504 | 1.0557 | 39.7808 | -12.5895 | 39.5606 | 9.2345 | Балхашская - пр/уз.Каргрэс - Балхашская
76 | 82.9426 | -7.2831 | -81.2281 | 14.8887 | 1.7145 | 7.6056 | 0.21851 | 0.2185 | 0.21851 | 1 | -57.0087 | 0.99185 | -62.388 | 2.1851 | -82.9426 | 7.2831 | -107.3323 | 16.7165 | ЮкГрэс 220 - пр/уз ЮкГРЭС ШУ
77 | -65.0301 | 24.7986 | 66.2281 | -19.4887 | 1.1981 | 5.31 | 0.18265 | 0.18266 | 0.18266 | 1 | -66.8769 | 0.99185 | -62.388 | 1.8266 | 65.0301 | -24.7986 | 88.2506 | -2.0975 | Шу 220 - пр/уз ЮкГРЭС ШУ
78 | 127.8827 | 53.9865 | -126.355 | -47.5732 | 1.5277 | 6.4133 | 0.35765 | 0.35774 | 0.35774 | 1.0186 | -63.9937 | 0.99044 | -66.2856 | 3.5774 | -127.8827 | -53.9865 | -113.5889 | 36.0501 | Алматы 220 - пр/уз Алматы Алма
79 | 181.4708 | 54.3682 | -178.645 | -42.4268 | 2.8258 | 11.9414 | 0.48645 | 0.48651 | 0.48651 | 1.022 | -62.9397 | 0.99044 | -66.2856 | 4.8651 | -181.4708 | -54.3682 | -195.1224 | 65.6308 | Алма 220 - пр/уз Алматы Алма
80 | 86.7558 | -5.3808 | -85.8545 | 9.2554 | 0.90131 | 3.8746 | 0.2272 | 0.2272 | 0.2272 | 1.004 | -83.9534 | 0.99742 | -86.5624 | 2.272 | -86.7558 | 5.3808 | -171.2869 | 62.1524 | Главная 220 - пр/уз Главная Кемин
81 | 240.8432 | 53.0983 | -234.1455 | -24.2554 | 6.6978 | 28.8429 | 0.61936 | 0.61936 | 0.61936 | 1.045 | -80.0417 | 0.99742 | -86.5624 | 6.1936 | -240.8432 | -53.0983 | -156.7672 | -96.4796 | Кемин 220 - пр/уз Главная Кемин
82 | -66.4242 | 35.0634 | 67.5804 | -30.1163 | 1.1562 | 4.9471 | 0.18863 | 0.18866 | 0.18866 | 1.045 | -80.0417 | 1.0292 | -76.2114 | 1.8866 | 66.4242 | -35.0634 | 126.4672 | -34.4636 | Кемин 220 - пр/уз Фрунзе Кемин
83 | 68.7371 | -25.1668 | -67.5804 | 30.1163 | 1.1566 | 4.9496 | 0.18869 | 0.18866 | 0.18869 | 1.0181 | -72.2793 | 1.0292 | -76.2114 | 1.8869 | -68.7371 | 25.1668 | -134.6938 | 60.6851 | Фрунзе 220 - пр/уз Фрунзе Кемин
84 | 50.4112 | -47.2427 | -49.9129 | 49.1939 | 0.4983 | 1.9512 | 0.17541 | 0.17536 | 0.17541 | 1.0336 | -74.8777 | 1.0488 | -76.3377 | 1.7541 | -50.4112 | 47.2427 | -53.0555 | 26.1572 | Жамбыл 220 - пр/уз Жамбыл Шымкент
85 | 5.6234 | 67.0975 | -5.1871 | -65.3939 | 0.43628 | 1.7035 | 0.16407 | 0.16414 | 0.16414 | 1.077 | -76.591 | 1.0488 | -76.3377 | 1.6414 | -5.6234 | -67.0975 | -2.326 | 18.8762 | Шымкент 220 - пр/уз Жамбыл Шымкент
86 | 298.2758 | 14.6236 | -288.409 | 26.8777 | 9.8668 | 41.5014 | 0.76981 | 0.76981 | 0.76981 | 1.0181 | -72.2793 | 0.98747 | -80.4123 | 7.6981 | -298.2758 | -14.6236 | -317.8113 | -38.3628 | Фрунзе 220 - пр/уз ГлавнаяФрунзе
87 | -111.5161 | 64.8312 | 113.409 | -56.8777 | 1.8929 | 7.9535 | 0.33717 | 0.33718 | 0.33718 | 1.004 | -83.9534 | 0.98747 | -80.4123 | 3.3718 | 111.5161 | -64.8312 | 129.0617 | -29.7727 | Главная 220 - пр/уз ГлавнаяФрунзе
88 | -58.3728 | 54.4739 | 58.946 | -51.9618 | 0.57321 | 2.512 | 0.19546 | 0.19551 | 0.19551 | 1.072 | -61.5761 | 1.0548 | -59.9352 | 1.9551 | 58.3728 | -54.4739 | 56.16 | 20.4767 | Робот - пр/уз ТалдыкорганРобот
89 | 98.9399 | -42.1391 | -97.846 | 46.9618 | 1.0939 | 4.8227 | 0.27007 | 0.27004 | 0.27007 | 1.045 | -57.3512 | 1.0548 | -59.9352 | 2.7007 | -98.9399 | 42.1391 | -96.1618 | 33.8909 | Талдыкорган 220 - пр/уз ТалдыкорганРобот
90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.045 | -41.192 | 0.99128 | -57.8361 | 0 | 0 | 0 | 0 | 0 | Мойынты - пр/уз МойынтыЮкгрэс
91 | 13.0519 | 4.4082 | -13 | -4.2 | 0.051938 | 0.20816 | 0.036153 | 0.036168 | 0.036168 | 1 | -57.0087 | 0.99128 | -57.8361 | 0.36168 | -13.0519 | -4.4082 | -13.0479 | 17.0664 | ЮкГрэс 220 - пр/уз МойынтыЮкгрэс
92 | -59.2444 | 0.66426 | 60.3994 | 4.3677 | 1.155 | 5.032 | 0.15322 | 0.15321 | 0.15322 | 1.0148 | -44.4756 | 1.0372 | -39.6757 | 1.5322 | 59.2444 | -0.66426 | 61.762 | -17.814 | Каражал 220 - Агадырь 220
93 | 116.5416 | -17.9111 | -114.3996 | 26.2132 | 2.142 | 8.3021 | 0.30492 | 0.30489 | 0.30492 | 1.0148 | -44.4756 | 1.0102 | -48.6645 | 3.0492 | -116.5416 | 17.9111 | -120.8172 | 46.3122 | Каражал 220 - пр/уз ЖезказганКаражал
94 | 94.676 | 77.1542 | -92.6004 | -69.1132 | 2.0756 | 8.0411 | 0.30011 | 0.30018 | 0.30018 | 1.068 | -46.206 | 1.0102 | -48.6645 | 3.0018 | -94.676 | -77.1542 | -89.0339 | -4.1877 | Жезказган 220 - пр/уз ЖезказганКаражал
95 | -79.2671 | -58.4712 | 80.7568 | 64.9926 | 1.4897 | 6.5214 | 0.25379 | 0.25377 | 0.25379 | 1.0186 | -63.9937 | 1.072 | -61.5761 | 2.5379 | 79.2671 | 58.4712 | 86.6174 | 1.5984 | Алматы 220 - Робот
96 | 63.9092 | 24.1258 | -63.5642 | -22.6233 | 0.34496 | 1.5025 | 0.16645 | 0.16646 | 0.16646 | 1.077 | -76.591 | 1.0637 | -77.6862 | 1.6646 | -63.9092 | -24.1258 | -63.8534 | 21.5352 | Шымкент 220 - ГНПС
97 | 44.6827 | 4.337 | -43.7958 | -0.9006 | 0.88691 | 3.4364 | 0.116 | 0.116 | 0.116 | 1.0156 | -81.4968 | 0.991 | -85.8983 | 1.16 | -44.6827 | -4.337 | -34.6887 | 0.42318 | Кентау - Ру-6
98 | 62.5581 | -25.0133 | -62.1895 | 26.4311 | 0.36857 | 1.4178 | 0.17841 | 0.17839 | 0.17841 | 0.991 | -85.8983 | 0.99405 | -87.1465 | 1.7841 | -62.5581 | 25.0133 | -40.3563 | -26.6459 | Ру-6 - пр/уз Ру-6/Кызылорда
99 | -59.024 | 61.7877 | 63.1572 | -45.5748 | 4.1332 | 16.2128 | 0.22425 | 0.2243 | 0.2243 | 1 | -88.0385 | 0.91123 | -77.5259 | 2.243 | 59.024 | -61.7877 | 68.1952 | -17.9861 | Кызылорда 220 - пр/уз Кызылорда-Кумколь
100 | 163.7258 | 19.5449 | -158.0078 | 4.5115 | 5.718 | 24.0564 | 0.40517 | 0.40518 | 0.40518 | 1.068 | -46.206 | 1.0238 | -54.6725 | 4.0518 | -163.7258 | -19.5449 | -171.2739 | 35.9621 | Жезказган 220 - Кумколь 220
101 | -10.4768 | -35.7674 | 10.4858 | 35.8073 | 0.0089427 | 0.03991 | 0.095043 | 0.095042 | 0.095043 | 1.0291 | -65.226 | 1.0302 | -65.2217 | 0.95043 | 10.4768 | 35.7674 | 37.8551 | -15.2218 | Медео - АТЭЦ-3
102 | 29.7196 | -22.8995 | -29.5232 | 23.7674 | 0.19649 | 0.86781 | 0.096668 | 0.096652 | 0.096668 | 1.0186 | -63.9937 | 1.0291 | -65.226 | 0.96668 | -29.7196 | 22.8995 | -2.2081 | -16.9459 | Алматы 220 - Медео
103 | -339.9697 | 70.2364 | 340.9779 | -64.6594 | 1.0082 | 5.577 | 0.88404 | 0.88405 | 0.88405 | 1.0305 | -66.1576 | 1.0302 | -65.2217 | 8.8405 | 339.9697 | -70.2364 | 185.4694 | 84.7257 | Коян-Кос - АТЭЦ-3
104 | 173.2561 | 40.6577 | -156.1572 | 26.5128 | 17.0989 | 67.1705 | 0.45616 | 0.45616 | 0.45616 | 1.0238 | -54.6725 | 0.91123 | -77.5259 | 4.5616 | -173.2561 | -40.6577 | -181.161 | -14.8105 | Кумколь 220 - пр/уз Кызылорда-Кумколь
105 | -204.5486 | -124.8324 | 206.1587 | 131.1558 | 1.6101 | 6.3234 | 0.6084 | 0.60838 | 0.6084 | 1.0336 | -74.8777 | 1.054 | -73.8052 | 6.084 | 204.5486 | 124.8324 | 209.1763 | -3.6909 | Жамбыл 220 - жгрэс-220
106 | 64.3805 | -36.6327 | -64.2331 | 37.311 | 0.14737 | 0.67839 | 0.19439 | 0.19439 | 0.19439 | 1 | -66.8769 | 1.0029 | -67.3891 | 1.9439 | -64.3805 | 36.6327 | -74.3685 | 34.0219 | Шу 220 - Аспара
107 | 56.2331 | -39.311 | -54.1156 | 47.6318 | 2.1175 | 8.3207 | 0.17955 | 0.1795 | 0.17955 | 1.0029 | -67.3891 | 1.054 | -73.8052 | 1.7955 | -56.2331 | 39.311 | -66.214 | 34.6723 | Аспара - жгрэс-220
108 | 4.1994 | -28.2883 | -4.0431 | 28.8615 | 0.1563 | 0.57318 | 0.072597 | 0.072563 | 0.072597 | 1.0338 | -73.3319 | 1.054 | -73.8052 | 0.72597 | -4.1994 | 28.2883 | 1.666 | 52.6148 | пр/уз жгрэс- Фрунзе - жгрэс-220
109 | -18.1994 | 26.2883 | 18.3949 | -25.5674 | 0.19552 | 0.72091 | 0.081164 | 0.081192 | 0.081192 | 1.0338 | -73.3319 | 1.0181 | -72.2793 | 0.81192 | 18.1994 | -26.2883 | 12.334 | -50.6149 | пр/уз жгрэс- Фрунзе - Фрунзе 220
110 | -5.6587 | 1.5299 | 5.6629 | -1.5184 | 0.004194 | 0.011517 | 0.014604 | 0.014614 | 0.014614 | 1.0533 | -78.0864 | 1.0528 | -77.8255 | 0.14614 | 5.6587 | -1.5299 | -52.4521 | 17.9044 | Жылга - Шымкентская
111 | -5.6413 | -6.0299 | 5.6539 | 6.0662 | 0.012656 | 0.036277 | 0.020572 | 0.020547 | 0.020572 | 1.0533 | -78.0864 | 1.0591 | -77.9127 | 0.20572 | 5.6413 | 6.0299 | -27.9796 | 23.7042 | Жылга - Пр/уз Шымкент-220/Жылга
112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0533 | -78.0864 | 1.045 | -70.6186 | 0 | 0 | 0 | 0 | 0 | Жылга - ТашкентТэс 220
113 | 125.0494 | -20.1575 | -122.445 | 35.9344 | 2.6044 | 15.777 | 0.31809 | 0.31808 | 0.31809 | 1.045 | -70.6186 | 1.0528 | -77.8255 | 3.1809 | -125.0494 | 20.1575 | -98.2217 | 38.1036 | ТашкентТэс 220 - Шымкентская
114 | 125.7131 | 98.2451 | -124.9332 | -93.3748 | 0.77991 | 4.8703 | 0.38877 | 0.38878 | 0.38878 | 1.077 | -76.591 | 1.0528 | -77.8255 | 3.8878 | -125.7131 | -98.2451 | -97.803 | -50.05 | Шымкент 220 - Шымкентская
115 | -45.5555 | -10.2227 | 46.4152 | 13.6588 | 0.85971 | 3.4361 | 0.12062 | 0.1206 | 0.12062 | 1.0158 | -81.6043 | 1.0528 | -77.8255 | 1.2062 | 45.5555 | 10.2227 | 49.7605 | -5.0633 | Миргалимсай - Шымкентская
116 | -10.2025 | 3.6763 | 10.2076 | -3.6592 | 0.0050868 | 0.017084 | 0.028017 | 0.028019 | 0.028019 | 1.0158 | -81.6043 | 1.0156 | -81.4968 | 0.28019 | 10.2025 | -3.6763 | 23.643 | 17.1076 | Миргалимсай - Кентау
117 | -32.1656 | 10.8998 | 32.475 | -9.7158 | 0.30942 | 1.184 | 0.087755 | 0.087774 | 0.087774 | 1.0156 | -81.4968 | 1.0135 | -79.394 | 0.87774 | 32.1656 | -10.8998 | 35.525 | 10.3208 | Кентау - пр/уз Кентау Жамбыл 220
118 | -75.475 | 3.4158 | 77.0125 | 2.5634 | 1.5375 | 5.9793 | 0.19564 | 0.19564 | 0.19564 | 1.0135 | -79.394 | 1.0336 | -74.8777 | 1.9564 | 75.475 | -3.4158 | 78.8309 | -9.5579 | пр/уз Кентау Жамбыл 220 - Жамбыл 220
119 | -223.6087 | 30.9908 | 225 | -18.6217 | 1.3913 | 12.3692 | 0.25556 | 0.25558 | 0.25558 | 1.02 | -68.759 | 1.02 | -65.5463 | 2.5558 | 223.6087 | -30.9908 | 223.5653 | 49.9796 | Фрунзе - ГЕНЕРАЦИЯ ЦА-1
120 | -54.9673 | -3.5239 | 55.758 | 6.5464 | 0.79076 | 3.0225 | 0.14504 | 0.14504 | 0.14504 | 0.9966 | -84.6484 | 1.0158 | -81.6043 | 1.4504 | 54.9673 | 3.5239 | 42.9459 | 18.387 | Жанакорган - Миргалимсай
121 | 36.9673 | 0.52387 | -36.7623 | 0.27222 | 0.20501 | 0.79608 | 0.097354 | 0.097355 | 0.097355 | 0.9966 | -84.6484 | 0.991 | -85.8983 | 0.97355 | -36.9673 | -0.52387 | -24.3695 | -15.1263 | Жанакорган - Ру-6
122 | 35.8211 | 14.8141 | -35.5539 | -13.7662 | 0.26715 | 1.0478 | 0.094455 | 0.094468 | 0.094468 | 1.077 | -76.591 | 1.0591 | -77.9127 | 0.94468 | -35.8211 | -14.8141 | -2.1361 | -3.5177 | Шымкент 220 - Пр/уз Шымкент-220/Жылга
123 | -41.976 | 30.2438 | 42.1895 | -29.4311 | 0.21352 | 0.81267 | 0.13577 | 0.1358 | 0.1358 | 1 | -88.0385 | 0.99405 | -87.1465 | 1.358 | 41.976 | -30.2438 | 32.8138 | 64.087 | Кызылорда 220 - пр/уз Ру-6/Кызылорда
124 | 43.5642 | 19.2233 | -42.7248 | -15.5776 | 0.83946 | 3.6457 | 0.11748 | 0.11751 | 0.11751 | 1.0637 | -77.6862 | 1.0156 | -81.4968 | 1.1751 | -43.5642 | -19.2233 | -43.527 | 20.0798 | ГНПС - Кентау
125 | 109.0134 | -19.1817 | -106.9658 | 28.132 | 2.0476 | 8.9502 | 0.27724 | 0.27724 | 0.27724 | 1.0477 | -26.9864 | 1.047 | -31.7485 | 2.7724 | -109.0134 | 19.1817 | -107.2139 | 8.268 | Оскаровка 220 - пр/уз Кар.ГРЭС-2 - Осакоровка
126 | -82.3581 | 50.0848 | 82.9658 | -47.432 | 0.60767 | 2.6528 | 0.23954 | 0.23955 | 0.23955 | 1.056 | -33.2995 | 1.047 | -31.7485 | 2.3955 | 82.3581 | -50.0848 | 80.9293 | -19.2168 | Кар.ГРЭС-2 - пр/уз Кар.ГРЭС-2 - Осакоровка
127 | -12.0445 | -33.5144 | 12.3454 | 34.819 | 0.30093 | 1.3046 | 0.091448 | 0.091408 | 0.091448 | 1.022 | -62.9397 | 1.0606 | -62.6856 | 0.91448 | 12.0445 | 33.5144 | 11.4358 | 29.6907 | Алма 220 - Чилик
128 | 63.1992 | 54.5877 | -62.3454 | -49.819 | 0.85382 | 4.7687 | 0.19744 | 0.19746 | 0.19746 | 1.11 | -60.4867 | 1.0606 | -62.6856 | 1.9746 | -63.1992 | -54.5877 | -62.0887 | -14.564 | Мойнакская ГЭС - Чилик
129 | 14.8008 | 18.7782 | -14.6366 | -17.8951 | 0.16413 | 0.88311 | 0.056529 | 0.056595 | 0.056595 | 1.11 | -60.4867 | 1.072 | -61.5761 | 0.56595 | -14.8008 | -18.7782 | -15.9189 | 3.2058 | Мойнакская ГЭС - Робот
130 | 86.0686 | 317.4885 | -83.9793 | -296.404 | 2.0893 | 21.0845 | 0.37615 | 0.38385 | 0.38385 | 0.99 | -17.0629 | 0.92675 | -17.721 | 3.8385 | -86.0686 | -317.4885 | -125.0771 | 124.0541 | Троицская ГРЭС - Сокол
131 | 798.4543 | 372.4767 | -783.7297 | -203.8317 | 14.7246 | 168.6451 | 0.98582 | 0.98589 | 0.98589 | 1.032 | 0 | 0.94847 | -10.4417 | 9.8589 | -798.4543 | -372.4767 | 221.6858 | 41.4318 | Ириклинская ГРЭС - Житикара
132 | 899.6042 | 198.1251 | -877.9319 | 12.008 | 21.6723 | 210.1331 | 1.0307 | 1.0307 | 1.0307 | 1.032 | 0 | 0.98363 | -13.2175 | 10.3071 | -899.6042 | -198.1251 | 99.8927 | 86.6544 | Ириклинская ГРЭС - Магнитагорская
133 | 293.1319 | -52.008 | -290.8603 | 71.8261 | 2.2716 | 19.8181 | 0.34949 | 0.34259 | 0.34949 | 0.98363 | -13.2175 | 0.99 | -17.0629 | 3.4949 | -293.1319 | 52.008 | 684.9655 | -96.1812 | Магнитагорская - Троицская ГРЭС
134 | 30.0397 | 408.2895 | -29.2083 | -396.3525 | 0.83141 | 11.937 | 0.46346 | 0.45446 | 0.46346 | 1.02 | -17.0554 | 0.99 | -17.0629 | 4.6346 | -30.0397 | -408.2895 | -1061.5629 | -9.6155 | ЮжУГРЭС - Троицская ГРЭС
135 | -546.1677 | -446.6586 | 549.9603 | 501.6804 | 3.7926 | 55.0218 | 0.84279 | 0.84271 | 0.84279 | 0.96668 | -20.1563 | 1.02 | -17.0554 | 8.4279 | 546.1677 | 446.6586 | -483.1505 | 20.7034 | Шагол - ЮжУГРЭС
136 | 531.0567 | 131.0475 | -529.1355 | -106.7664 | 1.9211 | 24.2811 | 0.65338 | 0.65339 | 0.65339 | 0.96668 | -20.1563 | 0.95395 | -22.6158 | 6.5339 | -531.0567 | -131.0475 | -908.6722 | 177.2567 | Шагол - Челябинск
137 | 187.8367 | -124.6086 | -186.8645 | 142.6018 | 0.97227 | 17.9932 | 0.28475 | 0.28453 | 0.28475 | 0.91408 | -18.7646 | 0.95395 | -22.6158 | 2.8475 | -187.8367 | 124.6086 | 187.2918 | 208.7636 | Костанай - Челябинск
138 | -67.2641 | -216.9675 | 67.711 | 220.6111 | 0.44689 | 3.6436 | 0.27571 | 0.27565 | 0.27571 | 0.95134 | -20.3219 | 0.96668 | -20.1563 | 2.7571 | 67.2641 | 216.9675 | -906.4949 | 152.2835 | Козырево - Шагол
139 | -72.7359 | 94.4892 | 73.3036 | -89.3947 | 0.56774 | 5.0945 | 0.14473 | 0.14496 | 0.14496 | 0.95134 | -20.3219 | 0.9209 | -18.4876 | 1.4496 | 72.7359 | -94.4892 | 488.4949 | 35.5221 | Козырево - Курган
140 | 58.7865 | 261.0031 | -56.1541 | -237.6109 | 2.6324 | 23.3922 | 0.30587 | 0.30614 | 0.30614 | 1.01 | -17.8723 | 0.9209 | -18.4876 | 3.0614 | -58.7865 | -261.0031 | 164.3257 | 121.2288 | АВРОРА 500 - Курган
141 | -33.1495 | -29.9006 | 33.2375 | 30.48 | 0.088048 | 0.57938 | 0.055976 | 0.055776 | 0.055976 | 0.9209 | -18.4876 | 0.93363 | -17.7898 | 0.55976 | 33.1495 | 29.9006 | -17.5924 | 133.1686 | Курган - Витязь
142 | -34.2375 | -193.6091 | 35.7538 | 211.481 | 1.5163 | 17.8719 | 0.24317 | 0.24281 | 0.24317 | 0.93363 | -17.7898 | 1.02 | -17.3425 | 2.4317 | 34.2375 | 193.6091 | -16.5764 | 182.3558 | Витязь - Восход
143 | -118.8827 | -128.1841 | 119.1294 | 130.6789 | 0.2467 | 2.4949 | 0.19791 | 0.19785 | 0.19791 | 1.02 | -17.3425 | 1.032 | -16.8355 | 1.9791 | 118.8827 | 128.1841 | 58.4854 | 50.4862 | Восход - ТАВРИЧЕСКАЯ
144 | -94.8712 | -30.6081 | 95.193 | 33.6405 | 0.3218 | 3.0324 | 0.11285 | 0.11275 | 0.11285 | 1.02 | -17.3425 | 1.034 | -15.6055 | 1.1285 | 94.8712 | 30.6081 | 102.9545 | 170.8661 | Восход - Барабинская
145 | 244.4051 | -87.7813 | -241.493 | 117.0858 | 2.9121 | 29.3045 | 0.29987 | 0.29971 | 0.29987 | 1 | -9.4249 | 1.034 | -15.6055 | 2.9987 | -244.4051 | 87.7813 | -252.2763 | 211.1855 | Заря - Барабинская
146 | -350.565 | 25.5111 | 353 | 32.443 | 2.435 | 57.954 | 0.40289 | 0.40288 | 0.40289 | 1.0074 | -8.785 | 1.016 | 0.70688 | 4.0289 | 350.565 | -25.5111 | 350.5814 | 201.8887 | Алтай - Генерация Сибири

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -131.7465 | -129.9552 | 132.1613 | 140.1964 | 0.41483 | 10.2412 | 0.20931 | 0.48155 | 1.0209 | -13.7225 | 1.05 | -12.201 | 36.6258
1 | -131.7465 | -129.9552 | 132.1613 | 140.1964 | 0.41483 | 10.2412 | 0.20931 | 0.48155 | 1.0209 | -13.7225 | 1.05 | -12.201 | 36.6258
2 | 3.4378 | -263.4246 | -2.8866 | 281.2466 | 0.55121 | 17.8221 | 0.29824 | 0.68535 | 1.02 | -19.026 | 1.077 | -19.1158 | 52.1263
3 | -279.1332 | -358.9673 | 279.8591 | 391.3806 | 0.72595 | 32.4133 | 0.5168 | 1.1801 | 1.016 | -7.8202 | 1.07 | -5.6734 | 56.1383
4 | 150.0079 | -332.2391 | -149.671 | 348.4658 | 0.33688 | 16.2267 | 0.43222 | 0.98478 | 0.97388 | -7.9767 | 1.0107 | -8.9195 | 46.8477
5 | 281.5731 | -313.7979 | -280.8717 | 353.3297 | 0.70146 | 39.5318 | 0.48115 | 1.0958 | 1.0118 | -22.5178 | 1.081 | -25.8056 | 83.3422
6 | 281.5731 | -313.7979 | -280.8717 | 353.3297 | 0.70146 | 39.5318 | 0.48115 | 1.0958 | 1.0118 | -22.5178 | 1.081 | -25.8056 | 83.3422
7 | 296.6936 | -234.0075 | -295.8671 | 268.532 | 0.8265 | 34.5245 | 0.43755 | 0.99864 | 0.99721 | -27.0254 | 1.05 | -30.6394 | 75.9544
8 | 39.4715 | 4.5051 | -39.1755 | -1.2361 | 0.29606 | 3.2691 | 0.044194 | 0.099166 | 1.038 | -39.2168 | 1.0372 | -39.6757 | 7.6394
9 | 99.4472 | 200.0766 | -98.9946 | -187.2482 | 0.45269 | 12.8283 | 0.24759 | 0.55585 | 1.042 | -55.851 | 1 | -57.0087 | 42.799
10 | 205.4257 | 40.8309 | -205.2928 | -30.6299 | 0.13284 | 10.201 | 0.24019 | 0.54472 | 1.0069 | -64.6616 | 1 | -66.8769 | 41.5196
11 | 197.3746 | 15.217 | -196.9524 | -5.7369 | 0.42219 | 9.4801 | 0.22377 | 0.50767 | 1.0215 | -61.6116 | 1.0186 | -63.9937 | 38.6801
12 | 197.3746 | 15.217 | -196.9524 | -5.7369 | 0.42219 | 9.4801 | 0.22377 | 0.50767 | 1.0215 | -61.6116 | 1.0186 | -63.9937 | 38.6801
13 | 202.938 | 96.2677 | -202.4759 | -84.8229 | 0.46207 | 11.4447 | 0.24891 | 0.5637 | 1.042 | -60.563 | 1.022 | -62.9397 | 43.026
14 | 202.938 | 96.2677 | -202.4759 | -84.8229 | 0.46207 | 11.4447 | 0.24891 | 0.5637 | 1.042 | -60.563 | 1.022 | -62.9397 | 43.026
15 | 265.5295 | -112.716 | -264.9399 | 131.5712 | 0.58958 | 18.8551 | 0.32656 | 0.74287 | 1.02 | -54.1947 | 1.045 | -57.3512 | 56.5015
16 | 188.1542 | -136.4398 | -187.8751 | 149.5117 | 0.27913 | 13.0719 | 0.26718 | 0.60961 | 1.0045 | -72.6929 | 1.0336 | -74.8777 | 46.3656
17 | 290.7909 | 13.555 | -290.2039 | 5.5553 | 0.58704 | 19.1102 | 0.32955 | 0.74821 | 1.02 | -68.759 | 1.0181 | -72.2793 | 56.9658
18 | 290.7909 | 13.555 | -290.2039 | 5.5553 | 0.58704 | 19.1102 | 0.32955 | 0.74821 | 1.02 | -68.759 | 1.0181 | -72.2793 | 56.9658
19 | 9.3446 | -110.4821 | -9.0494 | 114.815 | 0.29527 | 4.3329 | 0.12552 | 0.28923 | 1.02 | -70.4798 | 1.045 | -70.6186 | 21.9983
20 | 245.5783 | -297.3248 | -245.1833 | 333.653 | 0.395 | 36.3282 | 0.44263 | 1.0089 | 1.006 | -73.509 | 1.077 | -76.591 | 76.7364
21 | 245.5783 | -297.3248 | -245.1833 | 333.653 | 0.395 | 36.3282 | 0.44263 | 1.0089 | 1.006 | -73.509 | 1.077 | -76.591 | 76.7364
22 | -468.3614 | -79.6333 | 469.5 | 136.5691 | 1.1386 | 56.9359 | 0.56386 | 14.115 | 0.9729 | -6.9324 | 1 | -0.49583 | 77.6126
23 | -468.3614 | -79.6333 | 469.5 | 136.5691 | 1.1386 | 56.9359 | 0.56386 | 14.115 | 0.9729 | -6.9324 | 1 | -0.49583 | 77.6126
24 | -464.798 | -81.1316 | 465.8212 | 134.3042 | 1.0232 | 53.1726 | 0.55943 | 13.9949 | 0.97388 | -7.9767 | 1 | -1.8156 | 76.9517
25 | -471.331 | -81.2007 | 472.5691 | 136.9854 | 1.2381 | 55.7846 | 0.56708 | 14.2035 | 0.97388 | -7.9767 | 1 | -1.8156 | 78.0989
26 | -471.331 | -81.2007 | 472.5691 | 136.9854 | 1.2381 | 55.7846 | 0.56708 | 14.2035 | 0.97388 | -7.9767 | 1 | -1.8156 | 78.0989
27 | -471.331 | -81.2007 | 472.5691 | 136.9854 | 1.2381 | 55.7846 | 0.56708 | 14.2035 | 0.97388 | -7.9767 | 1 | -1.8156 | 78.0989
28 | -465.0444 | -79.6878 | 466.2357 | 132.871 | 1.1913 | 53.1831 | 0.55943 | 13.995 | 0.97388 | -7.9767 | 1 | -1.8156 | 76.9523
29 | -465.0444 | -79.6878 | 466.2357 | 132.871 | 1.1913 | 53.1831 | 0.55943 | 13.995 | 0.97388 | -7.9767 | 1 | -1.8156 | 76.9523
30 | 182.9515 | -192.0709 | -182.4018 | 209.8448 | 0.54972 | 17.774 | 0.29838 | 0.6832 | 1.0265 | -44.0697 | 1.068 | -46.206 | 51.9632
31 | -474.3169 | -343.5842 | 476 | 426.3945 | 1.6831 | 82.8103 | 1.5208 | 18.4479 | 1.0107 | -8.9195 | 1 | -3.1092 | 101.4369
32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0107 | -8.9195 | 1 | -3.1092 | 0
33 | -278.807 | -81.4539 | 279.6181 | 111.9869 | 0.81105 | 30.533 | 0.33011 | 8.6952 | 1.016 | -7.8202 | 1 | -2.6337 | 75.3024
34 | -278.8202 | -81.8145 | 279.6469 | 111.5923 | 0.82671 | 29.7778 | 0.33024 | 8.6917 | 1.016 | -7.8202 | 1 | -2.6337 | 75.2725
35 | -237.2638 | -70.2723 | 237.735 | 95.6671 | 0.47121 | 25.3948 | 0.28123 | 7.3976 | 1.016 | -7.8202 | 1 | -2.6337 | 64.0655
36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.016 | -7.8202 | 1 | -2.6337 | 0
37 | 45.5896 | -29.6966 | -45.5 | 32.0308 | 0.089647 | 2.3342 | 0.13842 | 0.2655 | 1.0316 | -67.354 | 1.1 | -68.5326 | 22.2575
38 | 45.5896 | -29.6966 | -45.5 | 32.0308 | 0.089647 | 2.3342 | 0.13842 | 0.2655 | 1.0316 | -67.354 | 1.1 | -68.5326 | 22.2575
39 | 39.5981 | -8.6389 | -39.5 | 10.6002 | 0.098142 | 1.9613 | 0.10253 | 0.19514 | 1.0374 | -42.3971 | 1.1 | -44.4179 | 32.7181
40 | 39.5981 | -8.6389 | -39.5 | 10.6002 | 0.098142 | 1.9613 | 0.10253 | 0.19514 | 1.0374 | -42.3971 | 1.1 | -44.4179 | 32.7181
41 | -7.6242 | -22.5846 | 7.7 | 23.6018 | 0.075832 | 1.0172 | 0.061099 | 0.11846 | 1.0238 | -54.6725 | 1.1 | -54.3054 | 19.8609
42 | -7.6242 | -22.5846 | 7.7 | 23.6018 | 0.075832 | 1.0172 | 0.061099 | 0.11846 | 1.0238 | -54.6725 | 1.1 | -54.3054 | 19.8609
43 | -90.7266 | -21.5095 | 91.5 | 39.7654 | 0.77345 | 18.2558 | 0.23171 | 0.47604 | 1.056 | -33.2995 | 1.1 | -26.9399 | 41.5697
44 | -90.7266 | -21.5095 | 91.5 | 39.7654 | 0.77345 | 18.2558 | 0.23171 | 0.47604 | 1.056 | -33.2995 | 1.1 | -26.9399 | 41.5697
45 | 38.8231 | -132.7108 | -38 | 150.9031 | 0.82308 | 18.1923 | 0.35222 | 0.74251 | 1.0302 | -65.2217 | 1.1 | -66.3684 | 58.9447

## res_ext_grid
| p_mw | q_mvar
0 | 101698.0585 | 40755.916

## res_load
| p_mw | q_mvar
0 | 10 | 0
1 | 2500 | 0
2 | 430 | 120
3 | 175 | 79
4 | 840 | 183
5 | 180 | 50
6 | 522.8 | 302
7 | 360 | 50
8 | 1050 | 98
9 | 20.5 | 5.1
10 | 67 | 20
11 | 3 | 2
12 | 12 | 2
13 | 825 | 102
14 | 202 | 27
15 | 81.4 | 12.2
16 | 420 | 76.2
17 | 195 | 25
18 | 660 | 70
19 | 368 | 60
20 | 255 | 60
21 | 154 | 55
22 | 304 | -25
23 | 103.5 | -99.4
24 | 2754 | 200
25 | 280 | 66.7
26 | 2295 | 25
27 | 130 | 32
28 | 6.4 | 2.1
29 | 25 | 15
30 | 33 | 3.2
31 | 0 | 0
32 | 232 | 10
33 | 385 | 114
34 | 174 | 11
35 | 135 | 40
36 | 24 | 9
37 | 173 | 49.7
38 | 38 | 18.8
39 | 9.1 | 1.3
40 | 54 | 30.4
41 | 1183.4 | 452.2
42 | 7.4 | 2.4
43 | 20.3 | 7.9
44 | 18 | 5.3
45 | 15 | 4.6
46 | 305 | 90
47 | 320 | 15
48 | 55.1 | 16.2
49 | 175 | 30
50 | 38.9 | 5
51 | 13 | 4.2
52 | 207 | 42.9
53 | 0 | 0
54 | 18 | 6
55 | 154 | 44
56 | 40 | 12
57 | 12 | 2
58 | 93 | -10
59 | 8 | 2
60 | 14 | 2
61 | 11.3 | 4.5
62 | 43 | 6.3
63 | 18 | 3
64 | 29.9 | 7.7
65 | 20 | 3
66 | 20 | 3.4
67 | 24 | 19.3
68 | 670 | 279
69 | 50 | 15
70 | 222 | 44.7
71 | 80.6 | 35.1
72 | 220 | 50
73 | 394 | 152
74 | 80 | 67.2
75 | 55.7 | 14
76 | 265 | 20
77 | 322 | 88
78 | 20 | 4
79 | 386.3 | 59.8
80 | 195.3 | 45.3
81 | 12 | 3
82 | 80 | 15
83 | 22 | 8
84 | 16 | 55
85 | 140 | -35
86 | -52.6 | 95
87 | 716 | -196
88 | -30 | 135
89 | 256 | -33.8
90 | 100000 | 40000
91 | 584.8 | 40
92 | 1 | 1
93 | 178 | 40
94 | 146.3 | -42.2
95 | 5 | 165

## res_shunt
| p_mw | q_mvar | vm_pu
0 | 0 | 960.7959 | 0.9677
1 | 0 | 494.1367 | 0.97388
2 | 0 | 379.2603 | 1.038
3 | 0 | 385.4462 | 1.042
4 | 0 | 183.6616 | 1.0215
5 | 0 | 192.1802 | 1.042
6 | 0 | 177.4163 | 1.0069
7 | 0 | 181.0296 | 1.02
8 | 0 | 174.5467 | 1.0045
9 | 0 | 175.8276 | 1.02
10 | 0 | 174.7872 | 1.02
11 | 0 | 178.1355 | 1.0118
12 | 0 | 174.4513 | 1.016
13 | 0 | 317.219 | 0.97602
14 | 0 | 505.398 | 1.0074
15 | 0 | 515.1505 | 1.01
16 | 0 | 295.9391 | 0.93159
17 | 0 | 286.5879 | 0.91408
18 | 0 | 146.8669 | 0.92675
19 | 0 | 277.3214 | 0.91811
20 | 0 | 189.6808 | 1.0265
21 | 0 | 176.868 | 1.02
22 | 0 | 351.9345 | 1.01
23 | 0 | 185.3142 | 1.032
24 | 0 | 172.6321 | 1.0048
25 | 0 | 19.6417 | 0.991
26 | 0 | 29.062 | 0.91123
27 | 0 | 301.9062 | 0.9209
28 | 0 | 157.4783 | 0.95134
29 | 0 | 160.1645 | 0.95395
30 | 0 | 154.729 | 0.94847
31 | 0 | 185.3142 | 1.032
32 | 0 | 162.1292 | 0.93363
33 | 0 | 182.07 | 1.02
34 | 0 | 187.1023 | 1.034
35 | 0 | 172 | 1

## res_gen
| p_mw | q_mvar | va_degree | vm_pu
0 | 0 | 1164.5988 | -39.2168 | 1.038
1 | 0 | 1100.8391 | -55.851 | 1.042
2 | 0 | 825.5212 | -60.563 | 1.042
3 | 0 | 481.6466 | -68.759 | 1.02
4 | 0 | -639.6374 | -73.509 | 1.006
5 | 0 | 216.3891 | -19.026 | 1.02
6 | 0 | 397.8405 | -39.5991 | 1.02
7 | 0 | -56.4273 | -54.1947 | 1.02
8 | 2934 | -28.8648 | -70.4798 | 1.02
9 | 0 | 101.4823 | -7.8202 | 1.016
10 | 1301 | 452.734 | -12.201 | 1.05
11 | 10 | 435.861 | -19.1158 | 1.077
12 | 1120 | 791.9638 | -5.6734 | 1.07
13 | 468 | 946.7169 | -25.8056 | 1.081
14 | 0 | 193.113 | -30.6394 | 1.05
15 | 0 | -188.1232 | -57.0087 | 1
16 | 0 | -58.663 | -66.8769 | 1
17 | 430 | 307.5945 | -83.9534 | 1.004
18 | 36 | 116.432 | -57.3512 | 1.045
19 | 450.3 | 238.1104 | -80.0417 | 1.045
20 | 776 | 164.6575 | -70.6186 | 1.045
21 | 203 | 1258.1983 | -8.876 | 1.01
22 | 3107 | 232.443 | 0.70688 | 1.016
23 | 46 | 59.6621 | -17.0629 | 0.99
24 | 2520 | 183.2463 | -65.5463 | 1.02
25 | 206 | 338.544 | -46.206 | 1.068
26 | 0 | 16.8242 | -41.192 | 1.045
27 | 501 | 441.3945 | -3.1092 | 1
28 | 0 | 0 | 0 | 0
29 | 250 | 962.6795 | -17.8723 | 1.01
30 | 0 | 915.4211 | -16.8355 | 1.032
31 | 946 | 577.197 | -33.4784 | 1.059
32 | 53 | 136.0315 | -88.0385 | 1
33 | 579 | 343.0616 | -68.5326 | 1.1
34 | 78 | 73.3659 | -60.4867 | 1.11
35 | 143 | 65.9003 | -44.4179 | 1.1
36 | 96 | 82.3036 | -54.3054 | 1.1
37 | 182 | 200.9031 | -66.3684 | 1.1
38 | 577 | 231.5307 | -26.9399 | 1.1
39 | 15 | -424.8299 | -62.9397 | 1.022
40 | 177 | 282.5262 | -61.5761 | 1.072
41 | 470 | 295.6491 | -73.8052 | 1.054
42 | 127 | 931.3884 | -76.591 | 1.077
43 | 809 | 322.2463 | -2.6337 | 1
44 | 2896 | 826.0023 | -1.8156 | 1
45 | 961 | 281.1383 | -0.49583 | 1
46 | 550 | 1044.9699 | -17.0554 | 1.02
47 | 0 | 274.7589 | -17.3425 | 1.02
48 | 0 | 295.6287 | -15.6055 | 1.034
49 | 190 | 219.0079 | -9.4249 | 1

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | gen | name | object
16 | gen | bus | uint32
17 | gen | p_mw | float64
18 | gen | vm_pu | float64
19 | gen | sn_mva | float64
20 | gen | min_q_mvar | float64
21 | gen | max_q_mvar | float64
22 | gen | scaling | float64
23 | gen | slack | bool
24 | gen | in_service | bool
25 | gen | slack_weight | float64
26 | gen | type | object
27 | gen | power_station_trafo | float64
28 | shunt | bus | uint32
29 | shunt | name | object
30 | shunt | q_mvar | float64
31 | shunt | p_mw | float64
32 | shunt | vn_kv | float64
33 | shunt | step | uint32
34 | shunt | max_step | uint32
35 | shunt | in_service | bool
36 | ext_grid | name | object
37 | ext_grid | bus | uint32
38 | ext_grid | vm_pu | float64
39 | ext_grid | va_degree | float64
40 | ext_grid | slack_weight | float64
41 | ext_grid | in_service | bool
42 | line | name | object
43 | line | std_type | object
44 | line | from_bus | uint32
45 | line | to_bus | uint32
46 | line | length_km | float64
47 | line | r_ohm_per_km | float64
48 | line | x_ohm_per_km | float64
49 | line | c_nf_per_km | float64
50 | line | g_us_per_km | float64
51 | line | max_i_ka | float64
52 | line | df | float64
53 | line | parallel | uint32
54 | line | type | object
55 | line | in_service | bool
56 | trafo | name | object
57 | trafo | std_type | object
58 | trafo | hv_bus | uint32
59 | trafo | lv_bus | uint32
60 | trafo | sn_mva | float64
61 | trafo | vn_hv_kv | float64
62 | trafo | vn_lv_kv | float64
63 | trafo | vk_percent | float64
64 | trafo | vkr_percent | float64
65 | trafo | pfe_kw | float64
66 | trafo | i0_percent | float64
67 | trafo | shift_degree | float64
68 | trafo | tap_side | object
69 | trafo | tap_neutral | float64
70 | trafo | tap_min | float64
71 | trafo | tap_max | float64
72 | trafo | tap_step_percent | float64
73 | trafo | tap_step_degree | float64
74 | trafo | tap_pos | float64
75 | trafo | tap_phase_shifter | bool
76 | trafo | parallel | uint32
77 | trafo | df | float64
78 | trafo | in_service | bool
79 | trafo | pt_percent | float64
80 | trafo | oltc | object
81 | res_bus | vm_pu | float64
82 | res_bus | va_degree | float64
83 | res_bus | p_mw | float64
84 | res_bus | q_mvar | float64
85 | res_line | p_from_mw | float64
86 | res_line | q_from_mvar | float64
87 | res_line | p_to_mw | float64
88 | res_line | q_to_mvar | float64
89 | res_line | pl_mw | float64
90 | res_line | ql_mvar | float64
91 | res_line | i_from_ka | float64
92 | res_line | i_to_ka | float64
93 | res_line | i_ka | float64
94 | res_line | vm_from_pu | float64
95 | res_line | va_from_degree | float64
96 | res_line | vm_to_pu | float64
97 | res_line | va_to_degree | float64
98 | res_line | loading_percent | float64
99 | res_trafo | p_hv_mw | float64
100 | res_trafo | q_hv_mvar | float64
101 | res_trafo | p_lv_mw | float64
102 | res_trafo | q_lv_mvar | float64
103 | res_trafo | pl_mw | float64
104 | res_trafo | ql_mvar | float64
105 | res_trafo | i_hv_ka | float64
106 | res_trafo | i_lv_ka | float64
107 | res_trafo | vm_hv_pu | float64
108 | res_trafo | va_hv_degree | float64
109 | res_trafo | vm_lv_pu | float64
110 | res_trafo | va_lv_degree | float64
111 | res_trafo | loading_percent | float64
112 | res_ext_grid | p_mw | float64
113 | res_ext_grid | q_mvar | float64
114 | res_load | p_mw | float64
115 | res_load | q_mvar | float64
116 | res_shunt | p_mw | float64
117 | res_shunt | q_mvar | float64
118 | res_shunt | vm_pu | float64
119 | res_gen | p_mw | float64
120 | res_gen | q_mvar | float64
121 | res_gen | va_degree | float64
122 | res_gen | vm_pu | float64