## parameters
| version | name | f_hz | sn_mva
0 | 2.9.0 | WACS | 50 | 1

## bus
| name | vn_kv | type | zone | in_service
25 | ЭГРЭС-1 | 500 | b | 2 | TRUE
26 | ЭК-1150 | 500 | b | 2 | TRUE
28 | ЭГРЕС-2 500 | 500 | b | 2 | TRUE
30 | еэк-20-бл5-8 | 20 | b | 2 | TRUE
31 | ЕЭК | 500 | b | 2 | TRUE
33 | ПС-ЕЭК 220 | 220 | b | 2 | TRUE
39 | ЭГРЭС-1 220 | 220 | b | 2 | TRUE
50 | эгрэс-1 бл3-2 | 20 | b | 2 | TRUE
51 | эгрэс-1 20 | 20 | b | 2 | TRUE
60 | эгрэс-2 20 | 20 | b | 2 | TRUE
63 | Ташкент | 500 | b | 18 | FALSE
129 | ЦГПП | 500 | b | 5 | TRUE
130 | ПС-ЦГПП 220 | 220 | b | 5 | TRUE
147 | АВРОРА 500 | 500 | b | 7 | TRUE
175 | Кокшетау | 500 | b | 6 | TRUE
180 | ПС-ЕГПП | 500 | b | 5 | TRUE
224 | Таш.ГРЭС | 500 | b | 18 | TRUE
240 | Усть-Каменогорск | 500 | b | 1 | TRUE
241 | У-К | 220 | b | 1 | TRUE
306 | Оскаровка 220 | 220 | b | 3 | TRUE
310 | Нура 220 | 220 | b | 3 | TRUE
325 | Нура | 500 | b | 3 | TRUE
355 | Кар.ГРЭС-2 | 220 | b | 3 | TRUE
356 | Кар.ГРЭС-2 110 | 110 | b | 3 | TRUE
455 | Кумколь 110 | 110 | b | 4 | TRUE
465 | Каражал 220 | 220 | b | 4 | TRUE
466 | Жезказган 220 | 220 | b | 4 | TRUE
467 | Кумколь 220 | 220 | b | 4 | TRUE
468 | Агадырь 220 | 220 | b | 4 | TRUE
469 | Агадырь | 500 | b | 4 | TRUE
472 | Балхашская 110 | 110 | b | 4 | TRUE
473 | Балхашская | 220 | b | 4 | TRUE
475 | Мойынты | 220 | b | 4 | TRUE
480 | ЖЕЗКАЗГАН | 500 | b | 4 | TRUE
576 | Сокол | 500 | b | 8 | TRUE
577 | Житикара | 500 | b | 8 | TRUE
590 | Костанай | 500 | b | 8 | TRUE
800 | Жамбыл | 500 | b | 11 | TRUE
801 | Жамбыл 220 | 220 | b | 11 | TRUE
805 | жгрэс-220 | 220 | b | 11 | TRUE
814 | Аспара | 220 | b | 9 | TRUE
830 | Шымкент | 500 | b | 12 | TRUE
831 | Шымкент 220 | 220 | b | 12 | TRUE
839 | Жылга | 220 | b | 12 | TRUE
840 | Кентау | 220 | b | 12 | TRUE
842 | Миргалимсай | 220 | b | 12 | TRUE
843 | Шымкентская | 220 | b | 12 | TRUE
862 | Кызылорда 220 | 220 | b | 13 | TRUE
865 | Жанакорган | 220 | b | 13 | TRUE
869 | Ру-6 | 220 | b | 13 | TRUE
900 | ЮКГРЭС | 500 | b | 9 | TRUE
901 | ЮкГрэс 220 | 220 | b | 9 | TRUE
902 | Алматы | 500 | b | 9 | TRUE
903 | Алматы 220 | 220 | b | 9 | TRUE
904 | АТЭЦ-3 | 220 | b | 9 | TRUE
905 | АТЭЦ-3 110 | 110 | b | 9 | TRUE
907 | Робот | 220 | b | 9 | TRUE
911 | Чилик | 220 | b | 9 | TRUE
912 | ПС-7 АХБК | 220 | b | 9 | TRUE
913 | ПС-7 АХБК 110 | 110 | b | 9 | TRUE
918 | Западная 220 | 220 | b | 9 | TRUE
928 | Медео | 220 | b | 9 | TRUE
932 | Шу 220 | 220 | b | 9 | TRUE
935 | Мойнакская ГЭС | 220 | b | 9 | TRUE
938 | Алма | 500 | b | 9 | TRUE
939 | Алма 220 | 220 | b | 9 | TRUE
953 | Коян-Кос | 220 | b | 9 | TRUE
980 | Семей | 500 | b | 19 | TRUE
981 | Семей 220 | 220 | b | 19 | TRUE
986 | Актогай | 500 | b | 1 | TRUE
987 | Талдыкорган | 500 | b | 10 | TRUE
988 | Талдыкорган 220 | 220 | b | 10 | TRUE
1621 | Рубцовск | 500 | b | 15 | TRUE
1630 | Барнаул | 500 | b | 15 | TRUE
1631 | Заря | 500 | b | 15 | TRUE
1636 | Генерация Сибири | 500 | b | 15 | TRUE
1660 | Алтай | 500 | b | 15 | TRUE
1817 | ТАВРИЧЕСКАЯ | 500 | b | 17 | TRUE
1850 | ИРТЫШСКАЯ | 500 | b | 17 | TRUE
1852 | Витязь | 500 | b | 17 | TRUE
1853 | Восход | 500 | b | 17 | TRUE
1916 | Главная 220 | 220 | b | 50 | TRUE
2918 | Фрунзе 220 | 220 | b | 50 | TRUE
2919 | Фрунзе | 500 | b | 50 | TRUE
2921 | ГЕНЕРАЦИЯ ЦА-1 | 500 | b | 51 | TRUE
2925 | ТашкентТэс 220 | 220 | b | 18 | TRUE
2952 | Кемин 220 | 220 | b | 51 | TRUE
4703 | Козырево | 500 | b | 16 | TRUE
4705 | Челябинск | 500 | b | 0 | TRUE
4727 | Курган | 500 | b | 16 | TRUE
4782 | Шагол | 500 | b | 16 | TRUE
4785 | Магнитагорская | 500 | b | 16 | TRUE
4790 | Ириклинская ГРЭС | 500 | b | 16 | TRUE
4799 | Троицская ГРЭС | 510 | b | 16 | TRUE
7201 | пр/уз. Семей У-К | 220 | b | 1 | TRUE
7202 | пр/уз. ЕЭК Семей | 220 | b | 20 | TRUE
7203 | пр/уз. Эгрэс-1 ЕЭК | 220 | b | 2 | TRUE
7204 | пр/уз.ЦГПП-ЭГРЭС-1 | 220 | b | 2 | TRUE
7205 | пр/уз.ЦГПП-Осакоровка | 220 | b | 5 | TRUE
7206 | пр/уз.ЭГРЭС 1 Осакоровка | 220 | b | 3 | TRUE
7208 | пр/уз.КарГРЭС-Нура | 220 | b | 3 | TRUE
7209 | пр/уз.Каргрэс-Каражал | 220 | b | 3 | TRUE
7210 | пр/уз.Каргрэс-Агадырь | 220 | b | 3 | TRUE
7211 | пр/уз.Каргрэс - Балхашская | 220 | b | 3 | TRUE
7212 | пр/уз ЮкГРЭС ШУ | 220 | b | 9 | TRUE
7213 | пр/уз Алматы Алма | 220 | b | 9 | TRUE
7214 | пр/уз Главная Кемин | 220 | b | 50 | TRUE
7215 | пр/уз Фрунзе Кемин | 220 | b | 51 | TRUE
7216 | пр/уз Жамбыл Шымкент | 220 | b | 12 | TRUE
7217 | пр/уз ГлавнаяФрунзе | 220 | b | 50 | TRUE
7218 | пр/уз ТалдыкорганРобот | 220 | b | 9 | TRUE
7219 | пр/уз МойынтыЮкгрэс | 220 | b | 9 | TRUE
7221 | пр/уз ЖезказганКаражал | 220 | b | 4 | TRUE
7223 | пр/уз жгрэс- Фрунзе | 220 | b | 11 | TRUE
7224 | пр/уз Кентау Жамбыл 220 | 220 | b | 12 | TRUE
7225 | Пр/уз Шымкент-220/Жылга | 220 | b | 12 | TRUE
7226 | пр/уз Ру-6/Кызылорда | 220 | b | 13 | TRUE
7227 | пр/уз Кызылорда-Кумколь | 220 | b | 14 | TRUE
7228 | ГНПС | 220 | b | 14 | TRUE
7229 | пр/уз Кар.ГРЭС-2 - Осакоровка | 220 | b | 3 | TRUE
9917 | Барабинская | 500 | b | 15 | TRUE
9932 | ЧУ | 500 | b | 9 | TRUE
10000 | ЮжУГРЭС | 500 | b | 16 | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
63 | Ташкент | 63 | 6964 | 3359 | 0 | 0 |  | 1 | FALSE | wye
1636 | Генерация Сибири | 1636 | 2754 | 200 | 0 | 0 |  | 1 | TRUE | wye
224 | Таш.ГРЭС | 224 | 2500 | 0 | 0 | 0 |  | 1 | TRUE | wye
2921 | ГЕНЕРАЦИЯ ЦА-1 | 2921 | 2295 | 25 | 0 | 0 |  | 1 | TRUE | wye
7208 | пр/уз.КарГРЭС-Нура | 7208 | 1183.4 | 452.2 | 0 | 0 |  | 1 | TRUE | wye
130 | ПС-ЦГПП 220 | 130 | 1050 | 98 | 0 | 0 |  | 1 | TRUE | wye
241 | У-К | 241 | 840 | 183 | 0 | 0 |  | 1 | TRUE | wye
1916 | Главная 220 | 1916 | 825 | 102 | 0 | 0 |  | 1 | TRUE | wye
4705 | Челябинск | 4705 | 716 | -196 | 0 | 0 |  | 1 | TRUE | wye
913 | ПС-7 АХБК 110 | 913 | 670 | 279 | 0 | 0 |  | 1 | TRUE | wye
2925 | ТашкентТэс 220 | 2925 | 660 | 70 | 0 | 0 |  | 1 | TRUE | wye
4785 | Магнитагорская | 4785 | 584.8 | 40 | 0 | 0 |  | 1 | TRUE | wye
33 | ПС-ЕЭК 220 | 33 | 522.8 | 302 | 0 | 0 |  | 1 | TRUE | wye
31 | ЕЭК | 31 | 430 | 120 | 0 | 0 |  | 1 | TRUE | wye
2952 | Кемин 220 | 2952 | 420 | 76.2 | 0 | 0 |  | 1 | TRUE | wye
356 | Кар.ГРЭС-2 110 | 356 | 394 | 152 | 0 | 0 |  | 1 | TRUE | wye
831 | Шымкент 220 | 831 | 386.3 | 59.8 | 0 | 0 |  | 1 | TRUE | wye
1817 | ТАВРИЧЕСКАЯ | 1817 | 385 | 114 | 0 | 0 |  | 1 | TRUE | wye
1630 | Барнаул | 1630 | 368 | 60 | 0 | 0 |  | 1 | TRUE | wye
39 | ЭГРЭС-1 220 | 39 | 360 | 50 | 0 | 0 |  | 1 | TRUE | wye
805 | жгрэс-220 | 805 | 322 | 88 | 0 | 0 |  | 1 | TRUE | wye
7214 | пр/уз Главная Кемин | 7214 | 320 | 15 | 0 | 0 |  | 1 | TRUE | wye
7213 | пр/уз Алматы Алма | 7213 | 305 | 90 | 0 | 0 |  | 1 | TRUE | wye
576 | Сокол | 576 | 304 | -25 | 0 | 0 |  | 1 | TRUE | wye
4799 | Троицская ГРЭС | 4799 | 280 | 66.7 | 0 | 0 |  | 1 | TRUE | wye
801 | Жамбыл 220 | 801 | 265 | 20 | 0 | 0 |  | 1 | TRUE | wye
577 | Житикара | 577 | 256 | -33.8 | 0 | 0 |  | 1 | TRUE | wye
175 | Кокшетау | 175 | 255 | 60 | 0 | 0 |  | 1 | TRUE | wye
147 | АВРОРА 500 | 147 | 232 | 10 | 0 | 0 |  | 1 | TRUE | wye
472 | Балхашская 110 | 472 | 222 | 44.7 | 0 | 0 |  | 1 | TRUE | wye
905 | АТЭЦ-3 110 | 905 | 220 | 50 | 0 | 0 |  | 1 | TRUE | wye
7221 | пр/уз ЖезказганКаражал | 7221 | 207 | 42.9 | 0 | 0 |  | 1 | TRUE | wye
988 | Талдыкорган 220 | 988 | 202 | 27 | 0 | 0 |  | 1 | TRUE | wye
843 | Шымкентская | 843 | 195.3 | 45.3 | 0 | 0 |  | 1 | TRUE | wye
2918 | Фрунзе 220 | 2918 | 195 | 25 | 0 | 0 |  | 1 | TRUE | wye
981 | Семей 220 | 981 | 180 | 50 | 0 | 0 |  | 1 | TRUE | wye
1853 | Восход | 1853 | 178 | 40 | 0 | 0 |  | 1 | TRUE | wye
1621 | Рубцовск | 1621 | 175 | 79 | 0 | 0 |  | 1 | TRUE | wye
7217 | пр/уз ГлавнаяФрунзе | 7217 | 175 | 30 | 0 | 0 |  | 1 | TRUE | wye
1850 | ИРТЫШСКАЯ | 1850 | 174 | 11 | 0 | 0 |  | 1 | TRUE | wye
7203 | пр/уз. Эгрэс-1 ЕЭК | 7203 | 173 | 49.7 | 0 | 0 |  | 1 | TRUE | wye
590 | Костанай | 590 | 154 | 55 | 0 | 0 |  | 1 | TRUE | wye
862 | Кызылорда 220 | 862 | 154 | 44 | 0 | 0 |  | 1 | TRUE | wye
9917 | Барабинская | 9917 | 146.3 | -42.2 | 0 | 0 |  | 1 | TRUE | wye
4703 | Козырево | 4703 | 140 | -35 | 0 | 0 |  | 1 | TRUE | wye
7201 | пр/уз. Семей У-К | 7201 | 135 | 40 | 0 | 0 |  | 1 | TRUE | wye
466 | Жезказган 220 | 466 | 130 | 32 | 0 | 0 |  | 1 | TRUE | wye
180 | ПС-ЕГПП | 180 | 103.5 | -99.4 | 0 | 0 |  | 1 | TRUE | wye
7227 | пр/уз Кызылорда-Кумколь | 7227 | 93 | -10 | 0 | 0 |  | 1 | TRUE | wye
918 | Западная 220 | 918 | 81.4 | 12.2 | 0 | 0 |  | 1 | TRUE | wye
455 | Кумколь 110 | 455 | 80.6 | 35.1 | 0 | 0 |  | 1 | TRUE | wye
51 | эгрэс-1 20 | 51 | 80 | 15 | 0 | 0 |  | 1 | TRUE | wye
903 | Алматы 220 | 903 | 80 | 67.2 | 0 | 0 |  | 1 | TRUE | wye
310 | Нура 220 | 310 | 67 | 20 | 0 | 0 |  | 1 | TRUE | wye
907 | Робот | 907 | 55.7 | 14 | 0 | 0 |  | 1 | TRUE | wye
7216 | пр/уз Жамбыл Шымкент | 7216 | 55.1 | 16.2 | 0 | 0 |  | 1 | TRUE | wye
7206 | пр/уз.ЭГРЭС 1 Осакоровка | 7206 | 54 | 30.4 | 0 | 0 |  | 1 | TRUE | wye
911 | Чилик | 911 | 50 | 15 | 0 | 0 |  | 1 | TRUE | wye
7224 | пр/уз Кентау Жамбыл 220 | 7224 | 43 | 6.3 | 0 | 0 |  | 1 | TRUE | wye
928 | Медео | 928 | 40 | 12 | 0 | 0 |  | 1 | TRUE | wye
7218 | пр/уз ТалдыкорганРобот | 7218 | 38.9 | 5 | 0 | 0 |  | 1 | TRUE | wye
7204 | пр/уз.ЦГПП-ЭГРЭС-1 | 7204 | 38 | 18.8 | 0 | 0 |  | 1 | TRUE | wye
465 | Каражал 220 | 465 | 33 | 3.2 | 0 | 0 |  | 1 | TRUE | wye
842 | Миргалимсай | 842 | 30 | 9.1 | 0 | 0 |  | 1 | TRUE | wye
7225 | Пр/уз Шымкент-220/Жылга | 7225 | 29.9 | 7.7 | 0 | 0 |  | 1 | TRUE | wye
50 | эгрэс-1 бл3-2 | 50 | 25 | 15 | 0 | 0 |  | 1 | TRUE | wye
7202 | пр/уз. ЕЭК Семей | 7202 | 24 | 9 | 0 | 0 |  | 1 | TRUE | wye
7229 | пр/уз Кар.ГРЭС-2 - Осакоровка | 7229 | 24 | 19.3 | 0 | 0 |  | 1 | TRUE | wye
60 | эгрэс-2 20 | 60 | 22 | 8 | 0 | 0 |  | 1 | TRUE | wye
306 | Оскаровка 220 | 306 | 20.5 | 5.1 | 0 | 0 |  | 1 | TRUE | wye
7210 | пр/уз.Каргрэс-Агадырь | 7210 | 20.3 | 7.9 | 0 | 0 |  | 1 | TRUE | wye
840 | Кентау | 840 | 20 | 4 | 0 | 0 |  | 1 | TRUE | wye
7226 | пр/уз Ру-6/Кызылорда | 7226 | 20 | 3 | 0 | 0 |  | 1 | TRUE | wye
7228 | ГНПС | 7228 | 20 | 3.4 | 0 | 0 |  | 1 | TRUE | wye
865 | Жанакорган | 865 | 18 | 3 | 0 | 0 |  | 1 | TRUE | wye
869 | Ру-6 | 869 | 18 | 6 | 0 | 0 |  | 1 | TRUE | wye
7211 | пр/уз.Каргрэс - Балхашская | 7211 | 18 | 5.3 | 0 | 0 |  | 1 | TRUE | wye
4727 | Курган | 4727 | 16 | 55 | 0 | 0 |  | 1 | TRUE | wye
7212 | пр/уз ЮкГРЭС ШУ | 7212 | 15 | 4.6 | 0 | 0 |  | 1 | TRUE | wye
7223 | пр/уз жгрэс- Фрунзе | 7223 | 14 | 2 | 0 | 0 |  | 1 | TRUE | wye
7219 | пр/уз МойынтыЮкгрэс | 7219 | 13 | 4.2 | 0 | 0 |  | 1 | TRUE | wye
30 | еэк-20-бл5-8 | 30 | 12 | 3 | 0 | 0 |  | 1 | TRUE | wye
932 | Шу 220 | 932 | 12 | 2 | 0 | 0 |  | 1 | TRUE | wye
953 | Коян-Кос | 953 | 12 | 2 | 0 | 0 |  | 1 | TRUE | wye
839 | Жылга | 839 | 11.3 | 4.5 | 0 | 0 |  | 1 | TRUE | wye
469 | Агадырь | 469 | 10 | 0 | 0 | 0 |  | 1 | TRUE | wye
7205 | пр/уз.ЦГПП-Осакоровка | 7205 | 9.1 | 1.3 | 0 | 0 |  | 1 | TRUE | wye
814 | Аспара | 814 | 8 | 2 | 0 | 0 |  | 1 | TRUE | wye
7209 | пр/уз.Каргрэс-Каражал | 7209 | 7.4 | 2.4 | 0 | 0 |  | 1 | TRUE | wye
475 | Мойынты | 475 | 6.4 | 2.1 | 0 | 0 |  | 1 | TRUE | wye
1631 | Заря | 1631 | 5 | 165 | 0 | 0 |  | 1 | TRUE | wye
901 | ЮкГрэс 220 | 901 | 3 | 2 | 0 | 0 |  | 1 | TRUE | wye
1852 | Витязь | 1852 | 1 | 1 | 0 | 0 |  | 1 | TRUE | wye

## gen
| name | bus | p_mw | vm_pu | sn_mva | min_q_mvar | max_q_mvar | scaling | slack | in_service | slack_weight | type | power_station_trafo
63 | Ташкент | 63 | 7018 | 1.014 |  | -2300 | 11500 | 1 | FALSE | FALSE | 0
1636 | Генерация Сибири | 1636 | 3107 | 1.016 |  | -1000 | 1000 | 1 | FALSE | TRUE | 0
224 | Таш.ГРЭС | 224 | 2934 | 1.02 |  | -1000 | 1000 | 1 | FALSE | TRUE | 0
51 | эгрэс-1 20 | 51 | 2896 | 1 |  | -430 | 1880 | 1 | FALSE | TRUE | 0
2921 | ГЕНЕРАЦИЯ ЦА-1 | 2921 | 2520 | 1.02 |  | -800 | 800 | 1 | FALSE | TRUE | 0
241 | У-К | 241 | 1301 | 1.05 |  | -383 | 896 | 1 | FALSE | TRUE | 0
33 | ПС-ЕЭК 220 | 33 | 1120 | 1.0727 |  | -150 | 804 | 1 | FALSE | TRUE | 0
60 | эгрэс-2 20 | 60 | 961 | 1 |  | -500 | 800 | 1 | FALSE | TRUE | 0
7208 | пр/уз.КарГРЭС-Нура | 7208 | 946 | 1.0591 |  | 113.9 | 718.8 | 1 | FALSE | TRUE | 0
30 | еэк-20-бл5-8 | 30 | 809 | 1 |  | -163 | 573 | 1 | FALSE | TRUE | 0
2925 | ТашкентТэс 220 | 2925 | 776 | 1.0455 |  | -500 | 920 | 1 | FALSE | TRUE | 0
4727 | Курган | 4727 | 696 | 1 |  |  |  | 1 | FALSE | TRUE | 0
913 | ПС-7 АХБК 110 | 913 | 579 | 1.1 |  | 92 | 437 | 1 | FALSE | TRUE | 0
356 | Кар.ГРЭС-2 110 | 356 | 577 | 1.1 |  | 35 | 140 | 1 | FALSE | TRUE | 0
4703 | Козырево | 4703 | 558 | 1 |  |  |  | 1 | FALSE | TRUE | 0
10000 | ЮжУГРЭС | 10000 | 550 | 1.02 |  | -300 | 300 | 1 | FALSE | TRUE | 0
50 | эгрэс-1 бл3-2 | 50 | 501 | 1 |  | -130 | 340 | 1 | FALSE | TRUE | 0
805 | жгрэс-220 | 805 | 470 | 1.0545 |  | 120 | 422 | 1 | FALSE | TRUE | 0
130 | ПС-ЦГПП 220 | 130 | 468 | 1.0818 |  | 40 | 250 | 1 | FALSE | TRUE | 0
2952 | Кемин 220 | 2952 | 450.3 | 1.0455 |  | -160 | 300 | 1 | FALSE | TRUE | 0
4782 | Шагол | 4782 | 439 | 1 |  |  |  | 1 | FALSE | TRUE | 0
1916 | Главная 220 | 1916 | 430 | 1.0045 |  | -100 | 100 | 1 | FALSE | TRUE | 0
147 | АВРОРА 500 | 147 | 250 | 1.01 |  | -64 | 152 | 1 | FALSE | TRUE | 0
466 | Жезказган 220 | 466 | 206 | 1.0682 |  | 25 | 232.5 | 1 | FALSE | TRUE | 0
1630 | Барнаул | 1630 | 203 | 1.01 |  |  |  | 1 | FALSE | TRUE | 0
1631 | Заря | 1631 | 190 | 1 |  |  |  | 1 | FALSE | TRUE | 0
905 | АТЭЦ-3 110 | 905 | 182 | 1.1 |  | 20 | 160 | 1 | FALSE | TRUE | 0
907 | Робот | 907 | 177 | 1.0727 |  |  | 168 | 1 | FALSE | TRUE | 0
7201 | пр/уз. Семей У-К | 7201 | 153 | 0 |  | -35 | 85 | 1 | FALSE | TRUE | 0
472 | Балхашская 110 | 472 | 143 | 1.1 |  | -30 | 88 | 1 | FALSE | TRUE | 0
831 | Шымкент 220 | 831 | 127 | 1.0773 |  |  | 100 | 1 | FALSE | TRUE | 0
455 | Кумколь 110 | 455 | 96 | 1.1 |  | -16.2 | 60.6 | 1 | FALSE | TRUE | 0
576 | Сокол | 576 | 94 | 1 |  |  | 0 | 1 | FALSE | TRUE | 0
935 | Мойнакская ГЭС | 935 | 78 | 1.1136 |  | -12 | 101 | 1 | FALSE | TRUE | 0
862 | Кызылорда 220 | 862 | 53 | 1 |  | -24 | 76 | 1 | FALSE | TRUE | 0
4799 | Троицская ГРЭС | 4799 | 46 | 0.99412 |  | -500 | 500 | 1 | FALSE | TRUE | 0
988 | Талдыкорган 220 | 988 | 36 | 1.0455 |  |  |  | 1 | FALSE | TRUE | 0
7204 | пр/уз.ЦГПП-ЭГРЭС-1 | 7204 | 30 | 1 |  |  |  | 1 | FALSE | TRUE | 0
939 | Алма 220 | 939 | 15 | 1.0227 |  | -10 | 10 | 1 | FALSE | TRUE | 0
7226 | пр/уз Ру-6/Кызылорда | 7226 | 13 | 1 |  |  |  | 1 | FALSE | TRUE | 0
7203 | пр/уз. Эгрэс-1 ЕЭК | 7203 | 12 | 1 |  |  | 9 | 1 | FALSE | TRUE | 0
981 | Семей 220 | 981 | 10 | 1.0773 |  |  |  | 1 | FALSE | TRUE | 0

## shunt
| bus | name | q_mvar | p_mw | vn_kv | step | max_step | in_service
26 | 26 | ЭК-1150 | 1023.4796 | 0 | 514.794 | 1 | 1 | TRUE
25 | 25 | ЭГРЭС-1 | 519.6328 | 0 | 515.0282 | 1 | 1 | TRUE
469 | 469 | Агадырь | 351.7855 | 0 | 519 | 1 | 1 | TRUE
900 | 900 | ЮКГРЭС | 354.5019 | 0 | 521 | 1 | 1 | TRUE
902 | 902 | Алматы | 175.5981 | 0 | 518.5651 | 1 | 1 | TRUE
938 | 938 | Алма | 177.251 | 0 | 521 | 1 | 1 | TRUE
9932 | 9932 | ЧУ | 173.4517 | 0 | 515.3861 | 1 | 1 | TRUE
2919 | 2919 | Фрунзе | 171.9975 | 0 | 513.2211 | 1 | 1 | TRUE
800 | 800 | Жамбыл | 171.5975 | 0 | 512.624 | 1 | 1 | TRUE
980 | 980 | Семей | 169.2077 | 0 | 509.0419 | 1 | 1 | TRUE
986 | 986 | Актогай | 167.93 | 0 | 507.1163 | 1 | 1 | TRUE
129 | 129 | ЦГПП | 173.3662 | 0 | 515.2591 | 1 | 1 | TRUE
31 | 31 | ЕЭК | 168.6713 | 0 | 508.2343 | 1 | 1 | TRUE
1621 | 1621 | Рубцовск | 332.8544 | 0 | 504.8421 | 1 | 1 | TRUE
1660 | 1660 | Алтай | 498.076 | 0 | 507.8748 | 1 | 1 | TRUE
1630 | 1630 | Барнаул | 504.1153 | 0 | 507.28 | 1 | 1 | TRUE
175 | 175 | Кокшетау | 334.9138 | 0 | 511.9189 | 1 | 1 | TRUE
590 | 590 | Костанай | 341.0197 | 0 | 510.9968 | 1 | 1 | TRUE
576 | 576 | Сокол | 170.0426 | 0 | 510.2962 | 1 | 1 | TRUE
180 | 180 | ПС-ЕГПП | 328.2522 | 0 | 501.3399 | 1 | 1 | TRUE
480 | 480 | ЖЕЗКАЗГАН | 179.8351 | 0 | 524.7841 | 1 | 1 | TRUE
2921 | 2921 | ГЕНЕРАЦИЯ ЦА-1 | 169.8453 | 0 | 510 | 1 | 1 | TRUE
147 | 147 | АВРОРА 500 | 335.8995 | 0 | 507.1461 | 1 | 1 | TRUE
1817 | 1817 | ТАВРИЧЕСКАЯ | 170.4354 | 0 | 510.8852 | 1 | 1 | TRUE
1850 | 1850 | ИРТЫШСКАЯ | 168.3533 | 0 | 507.755 | 1 | 1 | TRUE
869 | 869 | Ру-6 | 19.5566 | 0 | 227.4277 | 1 | 1 | TRUE
7227 | 7227 | пр/уз Кызылорда-Кумколь | 34.8007 | 0 | 214.5239 | 1 | 1 | TRUE
4727 | 4727 | Курган | 339.1735 | 0 | 509.6117 | 1 | 1 | TRUE
4703 | 4703 | Козырево | 170.8056 | 0 | 511.4398 | 1 | 1 | TRUE
4705 | 4705 | Челябинск | 174.2931 | 0 | 516.6346 | 1 | 1 | TRUE
577 | 577 | Житикара | 171.604 | 0 | 512.6337 | 1 | 1 | TRUE
4790 | 4790 | Ириклинская ГРЭС | 173.8652 | 0 | 516 | 1 | 1 | TRUE
1852 | 1852 | Витязь | 168.0635 | 0 | 507.3178 | 1 | 1 | TRUE
1853 | 1853 | Восход | 169.8453 | 0 | 510 | 1 | 1 | TRUE
9917 | 9917 | Барабинская | 174.5397 | 0 | 517 | 1 | 1 | TRUE
1631 | 1631 | Заря | 171.795 | 0 | 512.9188 | 1 | 1 | TRUE

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
4790 | BAZA | 4790 | 1.032 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
12531 | ЭГРЭС-1 - ЕЭК |  | 25 | 31 | 1 | 3.05 | 36.64 | 1.4732 | 0 | 217.4142 | 1 | 1 | ol | TRUE
225129 | ЭГРЭС-1 - ЦГПП |  | 25 | 129 | 1 | 7.3 | 89.75 | 3.3796 | 0 | 745.1023 | 1 | 1 | ol | TRUE
325325 | ЭГРЭС-1 - Нура |  | 25 | 325 | 1 | 8.3 | 78.3 | 3.3424 | 0 | 1133.7235 | 1 | 1 | ol | TRUE
4251817 | ЭГРЭС-1 - ТАВРИЧЕСКАЯ |  | 25 | 1817 | 1 | 11.8 | 108.2 | 4.5838 | 0 | 440.698 | 1 | 1 | ol | TRUE
52625 | ЭК-1150 - ЭГРЭС-1 |  | 26 | 25 | 1 | 0.31 | 3.81 | 0.15311 | 0 | 399.0779 | 1 | 1 | ol | TRUE
62625 | ЭК-1150 - ЭГРЭС-1 |  | 26 | 25 | 1 | 0.25 | 3.15 | 0.12637 | 0 | 482.7278 | 1 | 1 | ol | TRUE
726175 | ЭК-1150 - Кокшетау |  | 26 | 175 | 1 | 6.05 | 132.7 | 6.9648 | 0 | 608.979 | 1 | 1 | ol | TRUE
826469 | ЭК-1150 - Агадырь |  | 26 | 469 | 1 | 11.6 | 138.3 | 5.5941 | 0 | 1064.1459 | 1 | 1 | ol | TRUE
9261660 | ЭК-1150 - Алтай |  | 26 | 1660 | 1 | 14.79 | 212.33 | 9.123 | 0 | 440.0701 | 1 | 1 | ol | TRUE
102826 | ЭГРЕС-2 500 - ЭК-1150 |  | 28 | 26 | 1 | 0.81 | 11.75 | 0.3301 | 0 | 520.5556 | 1 | 1 | ol | TRUE
112826 | ЭГРЕС-2 500 - ЭК-1150 |  | 28 | 26 | 1 | 0.93 | 11.27 | 0.31291 | 0 | 541.7613 | 1 | 1 | ol | TRUE
12311621 | ЕЭК - Рубцовск |  | 31 | 1621 | 1 | 10.25 | 98.5 | 4.1063 | 0 | 247.1768 | 1 | 1 | ol | TRUE
13311850 | ЕЭК - ИРТЫШСКАЯ |  | 31 | 1850 | 1 | 7.62 | 76.8 | 3.0336 | 0 | 499.2597 | 1 | 1 | ol | TRUE
14337202 | ПС-ЕЭК 220 - пр/уз. ЕЭК Семей |  | 33 | 7202 | 1 | 4.94 | 52.48 | 2.0181 | 0 | 292.1162 | 1 | 1 | ol | TRUE
15337203 | ПС-ЕЭК 220 - пр/уз. Эгрэс-1 ЕЭК |  | 33 | 7203 | 1 | 4.43 | 18.775 | 1.7482 | 0 | 462.505 | 1 | 1 | ol | TRUE
16397203 | ЭГРЭС-1 220 - пр/уз. Эгрэс-1 ЕЭК |  | 39 | 7203 | 1 | 4.43 | 18.775 | 1.7482 | 0 | 67.0137 | 1 | 1 | ol | TRUE
17397204 | ЭГРЭС-1 220 - пр/уз.ЦГПП-ЭГРЭС-1 |  | 39 | 7204 | 1 | 13.62 | 60.625 | 2.0482 | 0 | 329.4184 | 1 | 1 | ol | TRUE
18397206 | ЭГРЭС-1 220 - пр/уз.ЭГРЭС 1 Осакоровка |  | 39 | 7206 | 1 | 17.395 | 68.48 | 1.4039 | 0 | 349.7053 | 1 | 1 | ol | TRUE
19129180 | ЦГПП - ПС-ЕГПП |  | 129 | 180 | 1 | 11.12 | 113.36 | 4.5488 | 0 | 289.2492 | 1 | 1 | ol | TRUE
201307204 | ПС-ЦГПП 220 - пр/уз.ЦГПП-ЭГРЭС-1 |  | 130 | 7204 | 1 | 13.62 | 60.625 | 2.0482 | 0 | 299.4027 | 1 | 1 | ol | TRUE
211307205 | ПС-ЦГПП 220 - пр/уз.ЦГПП-Осакоровка |  | 130 | 7205 | 1 | 2.865 | 11.525 | 2.0646 | 0 | 169.6706 | 1 | 1 | ol | TRUE
221471817 | АВРОРА 500 - ТАВРИЧЕСКАЯ |  | 147 | 1817 | 1 | 11.47 | 87.78 | 3.4378 | 0 | 221.7121 | 1 | 1 | ol | TRUE
231474727 | АВРОРА 500 - Курган |  | 147 | 4727 | 1 | 9.37 | 84.1 | 3.1959 | 0 | 237.8429 | 1 | 1 | ol | TRUE
24175147 | Кокшетау - АВРОРА 500 |  | 175 | 147 | 1 | 5 | 49.9 | 1.9513 | 0 | 399.9037 | 1 | 1 | ol | TRUE
25175590 | Кокшетау - Костанай |  | 175 | 590 | 1 | 5.02 | 106.96 | 5.561 | 0 | 647.736 | 1 | 1 | ol | TRUE
26180576 | ПС-ЕГПП - Сокол |  | 180 | 576 | 1 | 8.8 | 80 | 3.3996 | 0 | 10 | 1 | 1 | ol | FALSE
2722463 | Таш.ГРЭС - Ташкент |  | 224 | 63 | 1 | 0.45 | 5.81 | 0.20691 | 0 | 10 | 1 | 1 | ol | FALSE
28224830 | Таш.ГРЭС - Шымкент |  | 224 | 830 | 1 | 3 | 32.5 | 1.4484 | 0 | 420.6407 | 1 | 1 | ol | TRUE
292417201 | У-К - пр/уз. Семей У-К |  | 241 | 7201 | 1 | 3.075 | 24.27 | 1.9035 | 0 | 314.6409 | 1 | 1 | ol | TRUE
303067205 | Оскаровка 220 - пр/уз.ЦГПП-Осакоровка |  | 306 | 7205 | 1 | 2.86 | 11.52 | 2.0646 | 0 | 159.7863 | 1 | 1 | ol | TRUE
313067206 | Оскаровка 220 - пр/уз.ЭГРЭС 1 Осакоровка |  | 306 | 7206 | 1 | 17.395 | 68.48 | 1.4039 | 0 | 241.2247 | 1 | 1 | ol | TRUE
323067229 | Оскаровка 220 - пр/уз Кар.ГРЭС-2 - Осакоровка |  | 306 | 7229 | 1 | 8.88 | 38.87 | 0.76142 | 0 | 262.7601 | 1 | 1 | ol | TRUE
333107208 | Нура 220 - пр/уз.КарГРЭС-Нура |  | 310 | 7208 | 1 | 2.68 | 10.525 | 0.85787 | 0 | 617.2467 | 1 | 1 | ol | TRUE
34325469 | Нура - Агадырь |  | 325 | 469 | 1 | 6.86 | 79.4 | 3.1864 | 0 | 793.0665 | 1 | 1 | ol | TRUE
353557208 | Кар.ГРЭС-2 - пр/уз.КарГРЭС-Нура |  | 355 | 7208 | 1 | 2.68 | 10.52 | 0.85787 | 0 | 40.8868 | 1 | 1 | ol | TRUE
363557209 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Каражал |  | 355 | 7209 | 1 | 12.8 | 51.65 | 0.99714 | 0 | 274.7 | 1 | 1 | ol | TRUE
373557210 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Агадырь |  | 355 | 7210 | 1 | 9.005 | 36.565 | 0.73261 | 0 | 223.7213 | 1 | 1 | ol | TRUE
383557211 | Кар.ГРЭС-2 - пр/уз.Каргрэс - Балхашская |  | 355 | 7211 | 1 | 20.28 | 81.25 | 1.5873 | 0 | 167.5425 | 1 | 1 | ol | TRUE
393557229 | Кар.ГРЭС-2 - пр/уз Кар.ГРЭС-2 - Осакоровка |  | 355 | 7229 | 1 | 3.53 | 15.44 | 0.3024 | 0 | 208.9962 | 1 | 1 | ol | TRUE
40465468 | Каражал 220 - Агадырь 220 |  | 465 | 468 | 1 | 16.4 | 71.77 | 1.4059 | 0 | 180.3915 | 1 | 1 | ol | TRUE
414657209 | Каражал 220 - пр/уз.Каргрэс-Каражал |  | 465 | 7209 | 1 | 12.8 | 51.65 | 0.99714 | 0 | 245.8543 | 1 | 1 | ol | TRUE
424657221 | Каражал 220 - пр/уз ЖезказганКаражал |  | 465 | 7221 | 1 | 7.68 | 29.92 | 2.7445 | 0 | 315.5342 | 1 | 1 | ol | TRUE
43466467 | Жезказган 220 - Кумколь 220 |  | 466 | 467 | 1 | 11.606 | 48.977 | 4.0054 | 0 | 416.7978 | 1 | 1 | ol | TRUE
444667221 | Жезказган 220 - пр/уз ЖезказганКаражал |  | 466 | 7221 | 1 | 7.68 | 29.92 | 2.7445 | 0 | 246.0859 | 1 | 1 | ol | TRUE
454677227 | Кумколь 220 - пр/уз Кызылорда-Кумколь |  | 467 | 7227 | 1 | 27.385 | 107.645 | 2.2894 | 0 | 444.3277 | 1 | 1 | ol | TRUE
46468473 | Агадырь 220 - Балхашская |  | 468 | 473 | 1 | 23.67 | 99.68 | 2.0376 | 0 | 82.7528 | 1 | 1 | ol | TRUE
474687210 | Агадырь 220 - пр/уз.Каргрэс-Агадырь |  | 468 | 7210 | 1 | 9.005 | 36.56 | 0.73261 | 0 | 173.1875 | 1 | 1 | ol | TRUE
48469480 | Агадырь - ЖЕЗКАЗГАН |  | 469 | 480 | 1 | 12.6 | 123 | 4.8894 | 0 | 340.0774 | 1 | 1 | ol | TRUE
49469900 | Агадырь - ЮКГРЭС |  | 469 | 900 | 1 | 12.7 | 115.6 | 4.8576 | 0 | 779.2578 | 1 | 1 | ol | TRUE
50469900 | Агадырь - ЮКГРЭС |  | 469 | 900 | 1 | 11.5 | 118.41 | 4.6067 | 0 | 757.3364 | 1 | 1 | ol | TRUE
51473475 | Балхашская - Мойынты |  | 473 | 475 | 1 | 16.46 | 70.14 | 1.4219 | 0 | 54.5325 | 1 | 1 | ol | TRUE
524737211 | Балхашская - пр/уз.Каргрэс - Балхашская |  | 473 | 7211 | 1 | 20.28 | 81.25 | 1.5873 | 0 | 105.7225 | 1 | 1 | ol | TRUE
53475468 | Мойынты - Агадырь 220 |  | 475 | 468 | 1 | 12.8 | 54.2 | 1.1135 | 0 | 84.7989 | 1 | 1 | ol | TRUE
544757219 | Мойынты - пр/уз МойынтыЮкгрэс |  | 475 | 7219 | 1 | 13.245 | 57.565 | 1.1703 | 0 | 0 | 1 | 1 | ol | FALSE
55576577 | Сокол - Житикара |  | 576 | 577 | 1 | 4.7 | 53.5 | 2.1264 | 0 | 565.0733 | 1 | 1 | ol | TRUE
56590576 | Костанай - Сокол |  | 590 | 576 | 1 | 1.3 | 13.6 | 0.50613 | 0 | 645.3939 | 1 | 1 | ol | TRUE
575904705 | Костанай - Челябинск |  | 590 | 4705 | 1 | 4 | 75.3 | 4.5201 | 0 | 316.8833 | 1 | 1 | ol | TRUE
58800830 | Жамбыл - Шымкент |  | 800 | 830 | 1 | 4.1 | 51.6 | 1.9481 | 0 | 129.263 | 1 | 1 | ol | TRUE
59801805 | Жамбыл 220 - жгрэс-220 |  | 801 | 805 | 1 | 1.448 | 5.707 | 1.0342 | 0 | 510.951 | 1 | 1 | ol | TRUE
608017216 | Жамбыл 220 - пр/уз Жамбыл Шымкент |  | 801 | 7216 | 1 | 5.3954 | 21.463 | 1.7633 | 0 | 143.8301 | 1 | 1 | ol | TRUE
61814805 | Аспара - жгрэс-220 |  | 814 | 805 | 1 | 21.9 | 86.36 | 1.8182 | 0 | 182.5791 | 1 | 1 | ol | TRUE
62831843 | Шымкент 220 - Шымкентская |  | 831 | 843 | 1 | 1.72 | 10.75 | 0.24383 | 0 | 272.464 | 1 | 1 | ol | TRUE
638317216 | Шымкент 220 - пр/уз Жамбыл Шымкент |  | 831 | 7216 | 1 | 5.3954 | 21.463 | 1.7633 | 0 | 46.3317 | 1 | 1 | ol | TRUE
648317225 | Шымкент 220 - Пр/уз Шымкент-220/Жылга |  | 831 | 7225 | 1 | 9.98 | 39.675 | 0.82731 | 0 | 44.2969 | 1 | 1 | ol | TRUE
658317228 | Шымкент 220 - ГНПС |  | 831 | 7228 | 1 | 4.15 | 18.15 | 0.35547 | 0 | 164.1601 | 1 | 1 | ol | TRUE
66839843 | Жылга - Шымкентская |  | 839 | 843 | 1 | 6.55 | 41.4 | 0.88907 | 0 | 137.0951 | 1 | 1 | ol | TRUE
678392925 | Жылга - ТашкентТэс 220 |  | 839 | 2925 | 1 | 5.02 | 31.85 | 0.6777 | 0 | 0 | 1 | 1 | ol | FALSE
688397225 | Жылга - Пр/уз Шымкент-220/Жылга |  | 839 | 7225 | 1 | 9.98 | 39.67 | 0.82731 | 0 | 90.7082 | 1 | 1 | ol | TRUE
69840869 | Кентау - Ру-6 |  | 840 | 869 | 1 | 21.97 | 85.81 | 1.8077 | 0 | 111.8196 | 1 | 1 | ol | TRUE
708407224 | Кентау - пр/уз Кентау Жамбыл 220 |  | 840 | 7224 | 1 | 13.389 | 52.2869 | 1.5553 | 0 | 95.2907 | 1 | 1 | ol | TRUE
71842840 | Миргалимсай - Кентау |  | 842 | 840 | 1 | 2.16 | 8.4 | 0.17221 | 0 | 71.6359 | 1 | 1 | ol | TRUE
72842843 | Миргалимсай - Шымкентская |  | 842 | 843 | 1 | 19.7 | 79.3 | 1.5095 | 0 | 142.0375 | 1 | 1 | ol | TRUE
738627226 | Кызылорда 220 - пр/уз Ру-6/Кызылорда |  | 862 | 7226 | 1 | 3.855 | 15.055 | 1.35 | 0 | 188.9488 | 1 | 1 | ol | TRUE
748627227 | Кызылорда 220 - пр/уз Кызылорда-Кумколь |  | 862 | 7227 | 1 | 27.385 | 107.645 | 2.2894 | 0 | 219.0329 | 1 | 1 | ol | TRUE
75865842 | Жанакорган - Миргалимсай |  | 865 | 842 | 1 | 12.53 | 48.14 | 1.0091 | 0 | 116.9431 | 1 | 1 | ol | TRUE
76865869 | Жанакорган - Ру-6 |  | 865 | 869 | 1 | 7.21 | 28.31 | 0.59144 | 0 | 87.1997 | 1 | 1 | ol | TRUE
778697226 | Ру-6 - пр/уз Ру-6/Кызылорда |  | 869 | 7226 | 1 | 3.86 | 15.055 | 1.35 | 0 | 159.8731 | 1 | 1 | ol | TRUE
78900902 | ЮКГРЭС - Алматы |  | 900 | 902 | 1 | 9.35 | 85 | 3.5811 | 0 | 369.0762 | 1 | 1 | ol | TRUE
79900938 | ЮКГРЭС - Алма |  | 900 | 938 | 1 | 9.2 | 98.2 | 3.6543 | 0 | 281.7378 | 1 | 1 | ol | TRUE
809009932 | ЮКГРЭС - ЧУ |  | 900 | 9932 | 1 | 5.2 | 63.6 | 2.5084 | 0 | 761.1166 | 1 | 1 | ol | TRUE
819017212 | ЮкГрэс 220 - пр/уз ЮкГРЭС ШУ |  | 901 | 7212 | 1 | 11.97 | 53.21 | 1.0439 | 0 | 259.9392 | 1 | 1 | ol | TRUE
829017219 | ЮкГрэс 220 - пр/уз МойынтыЮкгрэс |  | 901 | 7219 | 1 | 13.24 | 57.56 | 1.1703 | 0 | 51.4076 | 1 | 1 | ol | TRUE
83902938 | Алматы - Алма |  | 902 | 938 | 1 | 1.8 | 19.5 | 0.72418 | 0 | 364.4418 | 1 | 1 | ol | TRUE
849029932 | Алматы - ЧУ |  | 902 | 9932 | 1 | 7.1 | 72.41 | 2.8999 | 0 | 312.3146 | 1 | 1 | ol | TRUE
85903904 | Алматы 220 - АТЭЦ-3 |  | 903 | 904 | 1 | 7 | 30.15 | 0.61754 | 0 | 71.6076 | 1 | 1 | ol | TRUE
86903907 | Алматы 220 - Робот |  | 903 | 907 | 1 | 7.71 | 33.81 | 0.6621 | 0 | 213.0826 | 1 | 1 | ol | TRUE
87903928 | Алматы 220 - Медео |  | 903 | 928 | 1 | 7.01 | 31.31 | 0.61436 | 0 | 67.8406 | 1 | 1 | ol | TRUE
889037213 | Алматы 220 - пр/уз Алматы Алма |  | 903 | 7213 | 1 | 3.975 | 16.95 | 6.0497 | 0 | 321.7076 | 1 | 1 | ol | TRUE
89904939 | АТЭЦ-3 - Алма 220 |  | 904 | 939 | 1 | 0.75 | 5.35 | 0.45201 | 0 | 661.0078 | 1 | 1 | ol | TRUE
909077218 | Робот - пр/уз ТалдыкорганРобот |  | 907 | 7218 | 1 | 5 | 22.175 | 1.7874 | 0 | 145.0163 | 1 | 1 | ol | TRUE
91912953 | ПС-7 АХБК - Коян-Кос |  | 912 | 953 | 1 | 0.565 | 3.15 | 0.25784 | 0 | 484.7404 | 1 | 1 | ol | TRUE
92918912 | Западная 220 - ПС-7 АХБК |  | 918 | 912 | 1 | 5 | 20 | 0.49021 | 0 | 209.3968 | 1 | 1 | ol | TRUE
939182952 | Западная 220 - Кемин 220 |  | 918 | 2952 | 1 | 9.27 | 40.58 | 0.79484 | 0 | 1211.9598 | 1 | 1 | ol | TRUE
94928904 | Медео - АТЭЦ-3 |  | 928 | 904 | 1 | 0.33 | 1.49 | 0.029285 | 0 | 101.834 | 1 | 1 | ol | TRUE
95932814 | Шу 220 - Аспара |  | 932 | 814 | 1 | 1.3 | 6 | 0.11778 | 0 | 200.144 | 1 | 1 | ol | TRUE
969321916 | Шу 220 - Главная 220 |  | 932 | 1916 | 1 | 16.8 | 72 | 1.4961 | 0 | 576.5124 | 1 | 1 | ol | TRUE
979327212 | Шу 220 - пр/уз ЮкГРЭС ШУ |  | 932 | 7212 | 1 | 11.97 | 53.21 | 1.0439 | 0 | 219.7974 | 1 | 1 | ol | TRUE
98935907 | Мойнакская ГЭС - Робот |  | 935 | 907 | 1 | 17.1 | 95.7 | 1.9577 | 0 | 86.325 | 1 | 1 | ol | TRUE
99935911 | Мойнакская ГЭС - Чилик |  | 935 | 911 | 1 | 7.3 | 40.9 | 0.83718 | 0 | 162.0115 | 1 | 1 | ol | TRUE
100939907 | Алма 220 - Робот |  | 939 | 907 | 1 | 2.1 | 14.2 | 0.2989 | 0 | 282.7102 | 1 | 1 | ol | TRUE
101939911 | Алма 220 - Чилик |  | 939 | 911 | 1 | 12 | 52.7 | 1.0314 | 0 | 78.3916 | 1 | 1 | ol | TRUE
1029397213 | Алма 220 - пр/уз Алматы Алма |  | 939 | 7213 | 1 | 3.975 | 16.95 | 6.0497 | 0 | 507.2153 | 1 | 1 | ol | TRUE
103953904 | Коян-Кос - АТЭЦ-3 |  | 953 | 904 | 1 | 0.425 | 2.375 | 0.19417 | 0 | 509.3247 | 1 | 1 | ol | TRUE
10498026 | Семей - ЭК-1150 |  | 980 | 26 | 1 | 10.1 | 122.52 | 4.8505 | 0 | 397.0908 | 1 | 1 | ol | TRUE
105980240 | Семей - Усть-Каменогорск |  | 980 | 240 | 1 | 5.72 | 58.55 | 2.2944 | 0 | 502.1389 | 1 | 1 | ol | TRUE
106980986 | Семей - Актогай |  | 980 | 986 | 1 | 9.84 | 120.42 | 4.5348 | 0 | 874.9283 | 1 | 1 | ol | TRUE
1079817201 | Семей 220 - пр/уз. Семей У-К |  | 981 | 7201 | 1 | 3.08 | 24.27 | 1.9035 | 0 | 403.1595 | 1 | 1 | ol | TRUE
1089817202 | Семей 220 - пр/уз. ЕЭК Семей |  | 981 | 7202 | 1 | 4.945 | 52.485 | 2.0181 | 0 | 221.8808 | 1 | 1 | ol | TRUE
109986987 | Актогай - Талдыкорган |  | 986 | 987 | 1 | 8.33 | 88.52 | 3.2936 | 0 | 868.5443 | 1 | 1 | ol | TRUE
110987938 | Талдыкорган - Алма |  | 987 | 938 | 1 | 5.91 | 62.76 | 2.3352 | 0 | 535.0456 | 1 | 1 | ol | TRUE
1119887218 | Талдыкорган 220 - пр/уз ТалдыкорганРобот |  | 988 | 7218 | 1 | 5 | 22.175 | 1.7874 | 0 | 245.4457 | 1 | 1 | ol | TRUE
1121621240 | Рубцовск - Усть-Каменогорск |  | 1621 | 240 | 1 | 4.34 | 44.02 | 1.7826 | 0 | 119.241 | 1 | 1 | ol | TRUE
11316301621 | Барнаул - Рубцовск |  | 1630 | 1621 | 1 | 10.3 | 105 | 4.3642 | 0 | 232.6227 | 1 | 1 | ol | TRUE
11416319917 | Заря - Барабинская |  | 1631 | 9917 | 1 | 10.8 | 110 | 4.3785 | 0 | 370.3308 | 1 | 1 | ol | TRUE
11516601630 | Алтай - Барнаул |  | 1660 | 1630 | 1 | 0.26 | 2.64 | 0.10536 | 0 | 179.6649 | 1 | 1 | ol | TRUE
11616601630 | Алтай - Барнаул |  | 1660 | 1630 | 1 | 0.19 | 1.97 | 0.078625 | 0 | 238.8781 | 1 | 1 | ol | TRUE
11716601631 | Алтай - Заря |  | 1660 | 1631 | 1 | 5.46 | 50.12 | 2.1073 | 0 | 180.0566 | 1 | 1 | ol | TRUE
11816601636 | Алтай - Генерация Сибири |  | 1660 | 1636 | 1 | 5 | 120 | 6.0481 | 0 | 478.9998 | 1 | 1 | ol | TRUE
11918171850 | ТАВРИЧЕСКАЯ - ИРТЫШСКАЯ |  | 1817 | 1850 | 1 | 3.42 | 35.28 | 1.3942 | 0 | 304.4337 | 1 | 1 | ol | TRUE
12018521853 | Витязь - Восход |  | 1852 | 1853 | 1 | 8.56 | 102.65 | 4.1502 | 0 | 208.3847 | 1 | 1 | ol | TRUE
12118531817 | Восход - ТАВРИЧЕСКАЯ |  | 1853 | 1817 | 1 | 2.1 | 21.85 | 0.87092 | 0 | 87.465 | 1 | 1 | ol | TRUE
12218539917 | Восход - Барабинская |  | 1853 | 9917 | 1 | 8.43 | 86.95 | 3.462 | 0 | 225.8305 | 1 | 1 | ol | TRUE
1231916903 | Главная 220 - Алматы 220 |  | 1916 | 903 | 1 | 19 | 82 | 1.6712 | 0 | 617.4874 | 1 | 1 | ol | TRUE
12419167214 | Главная 220 - пр/уз Главная Кемин |  | 1916 | 7214 | 1 | 5.82 | 25.065 | 0.51237 | 0 | 495.7157 | 1 | 1 | ol | TRUE
12519167217 | Главная 220 - пр/уз ГлавнаяФрунзе |  | 1916 | 7217 | 1 | 5.55 | 23.35 | 0.67961 | 0 | 366.2026 | 1 | 1 | ol | TRUE
12629187215 | Фрунзе 220 - пр/уз Фрунзе Кемин |  | 2918 | 7215 | 1 | 10.83 | 46.63 | 1.9064 | 0 | 383.5566 | 1 | 1 | ol | TRUE
12729187217 | Фрунзе 220 - пр/уз ГлавнаяФрунзе |  | 2918 | 7217 | 1 | 5.55 | 23.35 | 0.67961 | 0 | 832.7616 | 1 | 1 | ol | TRUE
1282919800 | Фрунзе - Жамбыл |  | 2919 | 800 | 1 | 6 | 69 | 2.5816 | 0 | 319.5887 | 1 | 1 | ol | TRUE
12929192921 | Фрунзе - ГЕНЕРАЦИЯ ЦА-1 |  | 2919 | 2921 | 1 | 7.1 | 64.2 | 2.5848 | 0 | 305.8679 | 1 | 1 | ol | TRUE
1302925843 | ТашкентТэс 220 - Шымкентская |  | 2925 | 843 | 1 | 8.58 | 52.04 | 1.1498 | 0 | 264.4606 | 1 | 1 | ol | TRUE
13129527214 | Кемин 220 - пр/уз Главная Кемин |  | 2952 | 7214 | 1 | 5.82 | 25.065 | 0.51237 | 0 | 472.678 | 1 | 1 | ol | TRUE
13229527215 | Кемин 220 - пр/уз Фрунзе Кемин |  | 2952 | 7215 | 1 | 10.83 | 46.63 | 1.9064 | 0 | 353.6325 | 1 | 1 | ol | TRUE
13347034727 | Козырево - Курган |  | 4703 | 4727 | 1 | 9.02 | 84.65 | 3.3933 | 0 | 592.1819 | 1 | 1 | ol | TRUE
13447034782 | Козырево - Шагол |  | 4703 | 4782 | 1 | 1.96 | 16.2 | 0.69394 | 0 | 1037.6561 | 1 | 1 | ol | TRUE
13547271852 | Курган - Витязь |  | 4727 | 1852 | 1 | 9.4 | 87.42 | 3.547 | 0 | 177.2686 | 1 | 1 | ol | TRUE
13647824705 | Шагол - Челябинск |  | 4782 | 4705 | 1 | 1.5 | 19 | 0.73213 | 0 | 1042.5046 | 1 | 1 | ol | TRUE
137478210000 | Шагол - ЮжУГРЭС |  | 4782 | 10000 | 1 | 1.78 | 25.87 | 1.2781 | 0 | 549.5441 | 1 | 1 | ol | TRUE
13847854799 | Магнитагорская - Троицская ГРЭС |  | 4785 | 4799 | 1 | 6.2 | 54.6 | 2.4351 | 0 | 822.7375 | 1 | 1 | ol | TRUE
1394790577 | Ириклинская ГРЭС - Житикара |  | 4790 | 577 | 1 | 5.05 | 57.9 | 2.3046 | 0 | 295.4819 | 1 | 1 | ol | TRUE
14047904785 | Ириклинская ГРЭС - Магнитагорская |  | 4790 | 4785 | 1 | 6.8 | 66 | 2.7057 | 0 | 189.8523 | 1 | 1 | ol | TRUE
1414799576 | Троицская ГРЭС - Сокол |  | 4799 | 576 | 1 | 4.92 | 50 | 1.9799 | 0 | 200.6079 | 1 | 1 | ol | TRUE
1427223805 | пр/уз жгрэс- Фрунзе - жгрэс-220 |  | 7223 | 805 | 1 | 9.885 | 37.125 | 0.82142 | 0 | 131.544 | 1 | 1 | ol | TRUE
14372232918 | пр/уз жгрэс- Фрунзе - Фрунзе 220 |  | 7223 | 2918 | 1 | 9.885 | 37.125 | 0.82142 | 0 | 163.1285 | 1 | 1 | ol | TRUE
1447224801 | пр/уз Кентау Жамбыл 220 - Жамбыл 220 |  | 7224 | 801 | 1 | 13.389 | 52.2869 | 1.5553 | 0 | 209.4548 | 1 | 1 | ol | TRUE
1457228840 | ГНПС - Кентау |  | 7228 | 840 | 1 | 20.27 | 88.72 | 1.7379 | 0 | 116.6029 | 1 | 1 | ol | TRUE
14699322919 | ЧУ - Фрунзе |  | 9932 | 2919 | 1 | 2.82 | 28.85 | 1.1523 | 0 | 788.3941 | 1 | 1 | ol | TRUE
147100004799 | ЮжУГРЭС - Троицская ГРЭС |  | 10000 | 4799 | 1 | 1.29 | 18.64 | 0.96483 | 0 | 1202.5117 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service | pt_percent | oltc | Unnamed: 26 | Unnamed: 27 | Unnamed: 28
12539 | ЭГРЭС-1 - ЭГРЭС-1 220 |  | 25 | 39 | 801 | 500 | 220 | 8.6 | 0.025121 | 297.45 | 0.15 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 1 | 12539
22551 | ЭГРЭС-1 - эгрэс-1 20 |  | 25 | 51 | 630 | 525 | 20 | 14.2 | 0.20386 | 270.97 | 0.058 | 0 | [7 empty] | FALSE | 3 | 1 | TRUE |  | FALSE |  | 2 | 22551
32860 | ЭГРЕС-2 500 - эгрэс-2 20 |  | 28 | 60 | 630 | 525 | 20 | 14.7 | 0.20317 | 380 | 0.21 | 0 | [7 empty] | FALSE | 2 | 1 | TRUE |  | FALSE |  | 3 | 32860
43130 | ЕЭК - еэк-20-бл5-8 |  | 31 | 30 | 400 | 525 | 20 | 12.6 | 0.20075 | 370 | 0.54 | 0 | [7 empty] | FALSE | 2 | 1 | TRUE |  | FALSE |  | 4 | 43130
53133 | ЕЭК - ПС-ЕЭК 220 |  | 31 | 33 | 801 | 500 | 237 | 11.9 | 0.17066 | 273.3 | 0.291 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 5 | 53133
63950 | ЭГРЭС-1 220 - эгрэс-1 бл3-2 |  | 39 | 50 | 630 | 242 | 20 | 12.5 | 0.20635 | 380 | 0.35 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 6 | 63950
7129130 | ЦГПП - ПС-ЦГПП 220 |  | 129 | 130 | 501 | 525 | 230 | 11 | 0.14781 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 7 | 7129130
8129130 | ЦГПП - ПС-ЦГПП 220 |  | 129 | 130 | 501 | 525 | 230 | 11 | 0.14781 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 8 | 8129130
92242925 | Таш.ГРЭС - ТашкентТэс 220 |  | 224 | 2925 | 500 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 9 | 92242925
10240241 | Усть-Каменогорск - У-К |  | 240 | 241 | 500 | 500 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 10 | 10240241
11240241 | Усть-Каменогорск - У-К |  | 240 | 241 | 500 | 500 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 11 | 11240241
12325310 | Нура - Нура 220 |  | 325 | 310 | 500 | 500 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 12 | 12325310
13355356 | Кар.ГРЭС-2 - Кар.ГРЭС-2 110 |  | 355 | 356 | 240 | 242 | 121 | 12.3 | 0.28667 | 452 | 3 | 0 | [7 empty] | FALSE | 2 | 1 | TRUE |  | FALSE |  | 13 | 13355356
14467455 | Кумколь 220 - Кумколь 110 |  | 467 | 455 | 125 | 220 | 110 | 11 | 0.252 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 14 | 14467455
15469468 | Агадырь - Агадырь 220 |  | 469 | 468 | 500 | 500 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 15 | 15469468
16473472 | Балхашская - Балхашская 110 |  | 473 | 472 | 125 | 230 | 121 | 11 | 0.252 | 65 | 0.4 | 0 | [7 empty] | FALSE | 2 | 1 | TRUE |  | FALSE |  | 16 | 16473472
17480466 | ЖЕЗКАЗГАН - Жезказган 220 |  | 480 | 466 | 500 | 500 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 17 | 17480466
18800801 | Жамбыл - Жамбыл 220 |  | 800 | 801 | 501 | 525 | 230 | 10.5 | 0.060413 | 206.49 | 0.35 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 18 | 18800801
19830831 | Шымкент - Шымкент 220 |  | 830 | 831 | 501 | 525 | 230 | 9.66 | 0.062535 | 306 | 0.92 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 19 | 19830831
20830831 | Шымкент - Шымкент 220 |  | 830 | 831 | 501 | 525 | 230 | 9.66 | 0.062535 | 306 | 0.92 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 20 | 20830831
21900901 | ЮКГРЭС - ЮкГрэс 220 |  | 900 | 901 | 500 | 525 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 21 | 21900901
22902903 | Алматы - Алматы 220 |  | 902 | 903 | 500 | 525 | 230 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 22 | 22902903
23902903 | Алматы - Алматы 220 |  | 902 | 903 | 500 | 525 | 230 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 23 | 23902903
24904905 | АТЭЦ-3 - АТЭЦ-3 110 |  | 904 | 905 | 240 | 230 | 121 | 20 | 0.526 | 450 | 3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 24 | 24904905
25912913 | ПС-7 АХБК - ПС-7 АХБК 110 |  | 912 | 913 | 250 | 230 | 121 | 11 | 0.208 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 25 | 25912913
26938939 | Алма - Алма 220 |  | 938 | 939 | 501 | 525 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 26 | 26938939
27938939 | Алма - Алма 220 |  | 938 | 939 | 501 | 525 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 27 | 27938939
28980981 | Семей - Семей 220 |  | 980 | 981 | 500 | 525 | 230 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 28 | 28980981
29987988 | Талдыкорган - Талдыкорган 220 |  | 987 | 988 | 501 | 525 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 29 | 29987988
3029192918 | Фрунзе - Фрунзе 220 |  | 2919 | 2918 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 30 | 3029192918
3129192918 | Фрунзе - Фрунзе 220 |  | 2919 | 2918 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 31 | 3129192918
329932932 | ЧУ - Шу 220 |  | 9932 | 932 | 501 | 525 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE |  | 32 | 329932932

## measurement
| name | measurement_type | element_type | element | value | std_dev | side
25 | ЭГРЭС-1 | v | bus | 25 | 1.036 | 0.051802
26 | ЭК-1150 | v | bus | 26 | 1.0413 | 0.052067
28 | ЭГРЕС-2 500 | v | bus | 28 | 1.0343 | 0.051716
31 | ЕЭК | v | bus | 31 | 1.0243 | 0.051213
33 | ПС-ЕЭК 220 | v | bus | 33 | 1.0468 | 0.052341
39 | ЭГРЭС-1 220 | v | bus | 39 | 1.0509 | 0.052543
129 | ЦГПП | v | bus | 129 | 1.0349 | 0.051747
130 | ПС-ЦГПП 220 | v | bus | 130 | 1.0974 | 0.05487
147 | АВРОРА 500 | v | bus | 147 | 1.0308 | 0.051541
175 | Кокшетау | v | bus | 175 | 1.0084 | 0.050422
180 | ПС-ЕГПП | v | bus | 180 | 1.0221 | 0.051107
240 | Усть-Каменогорск | v | bus | 240 | 1.023 | 0.051148
241 | У-К | v | bus | 241 | 1.0577 | 0.052884
306 | Оскаровка 220 | v | bus | 306 | 1.0869 | 0.054345
310 | Нура 220 | v | bus | 310 | 1.065 | 0.05325
325 | Нура | v | bus | 325 | 1.039 | 0.051952
355 | Кар.ГРЭС-2 | v | bus | 355 | 1.0532 | 0.052659
465 | Каражал 220 | v | bus | 465 | 1.0136 | 0.050682
466 | Жезказган 220 | v | bus | 466 | 1.0887 | 0.054436
467 | Кумколь 220 | v | bus | 467 | 1.0778 | 0.053889
468 | Агадырь 220 | v | bus | 468 | 1.1029 | 0.055145
469 | Агадырь | v | bus | 469 | 1.0349 | 0.051747
473 | Балхашская | v | bus | 473 | 1.0677 | 0.053386
480 | ЖЕЗКАЗГАН | v | bus | 480 | 1.0354 | 0.05177
576 | Сокол | v | bus | 576 | 1.0322 | 0.05161
577 | ПС 500 кВ Житикара - СШ 500 кВ | v | bus | 577 | 1.0354 | 0.05177
590 | Костанай | v | bus | 590 | 1.0263 | 0.051313
800 | Жамбыл | v | bus | 800 | 1.0016 | 0.05008
801 | Жамбыл 220 | v | bus | 801 | 1.0504 | 0.052518
805 | жгрэс-220 | v | bus | 805 | 1.059 | 0.052948
830 | Шымкент | v | bus | 830 | 0.99382 | 0.049691
831 | Шымкент 220 | v | bus | 831 | 1.0782 | 0.053911
840 | Кентау | v | bus | 840 | 1.0618 | 0.053089
842 | Миргалимсай | v | bus | 842 | 1.0528 | 0.052639
843 | Шымкентская | v | bus | 843 | 1.049 | 0.05245
862 | Кызылорда 220 | v | bus | 862 | 1.0664 | 0.053318
865 | Жанакорган | v | bus | 865 | 1.0667 | 0.053334
869 | Ру-6 | v | bus | 869 | 1.0686 | 0.05343
900 | ЮКГРЭС | v | bus | 900 | 1.0359 | 0.051793
901 | ЮкГрэс 220 | v | bus | 901 | 1.0878 | 0.054391
902 | Алматы | v | bus | 902 | 1.0308 | 0.051541
903 | Алматы 220 | v | bus | 903 | 1.076 | 0.053798
904 | АТЭЦ-3 | v | bus | 904 | 1.0625 | 0.053125
907 | Робот | v | bus | 907 | 1.0605 | 0.053025
912 | ПС-7 АХБК | v | bus | 912 | 1.0195 | 0.050977
918 | Западная 220 | v | bus | 918 | 1.0156 | 0.05078
932 | Шу 220 | v | bus | 932 | 1.0686 | 0.053432
938 | Алма | v | bus | 938 | 1.0435 | 0.052175
939 | Алма 220 | v | bus | 939 | 1.0596 | 0.05298
980 | Семей | v | bus | 980 | 1.0303 | 0.051514
981 | Семей 220 | v | bus | 981 | 1.018 | 0.050902
986 | Актогай | v | bus | 986 | 1.0368 | 0.051839
987 | Талдыкорган | v | bus | 987 | 1.0251 | 0.051256
988 | Талдыкорган 220 | v | bus | 988 | 1.0751 | 0.053755
1621 | Рубцовск | v | bus | 1621 | 1.0418 | 0.052091
1630 | Барнаул | v | bus | 1630 | 1.0275 | 0.051377
1631 | ПС 500 кВ Заря - СШ 500 кВ | v | bus | 1631 | 1.0231 | 0.051157
1660 | Алтай | v | bus | 1660 | 1.0316 | 0.051579
1817 | ТАВРИЧЕСКАЯ | v | bus | 1817 | 1.0301 | 0.051503
1850 | ИРТЫШСКАЯ | v | bus | 1850 | 1.0342 | 0.051709
2925 | ТашкентТэс 220 | v | bus | 2925 | 1.042 | 0.0521
9932 | ЧУ | v | bus | 9932 | 1.0084 | 0.050422
1000001 | эгрэс-1 бл3-2 | p | bus | 50 | 353.72 | 17.686
1000002 | эгрес-1 20 | p | bus | 51 | 2222.5 | 111.125
1000003 | эгрэс-2 20 | p | bus | 60 | 398.88 | 19.944
1000004 | Таш.ГРЭС | p | bus | 224 | 456 | 22.8
1000005 | Оскаровка 220 | p | bus | 306 | -8.25 | 0.04
1000006 | Нура 220 | p | bus | 310 | -27.41 | 0.04
1000007 | Кар.ГРЭС-2 110 | p | bus | 356 | 300.05 | 15.0025
1000008 | Кумколь 110 | p | bus | 455 | 117.21 | 5.8605
1000009 | Агадырь 220 | p | bus | 468 | -73.41 | 0.04
1000010 | Балхашская 110 | p | bus | 472 | 105.62 | 5.281
1000011 | ПС 500 кВ Житикара - СШ 500 кВ | p | bus | 577 | -159 | 0.04
1000012 | Жамбыл 220 | p | bus | 801 | -217.01 | 0.04
1000013 | жгрэс-220 | p | bus | 805 | 226.01 | 11.3005
1000014 | Шымкент 220 | p | bus | 831 | -123.39 | 0.04
1000015 | Кентау | p | bus | 840 | -26.86 | 0.04
1000016 | Миргалимсай | p | bus | 842 | -17.29 | 0.04
1000017 | Шымкентская | p | bus | 843 | -182.21 | 0.04
1000018 | Кызылорда 220 | p | bus | 862 | -16.08 | 0.04
1000019 | Ру-6 | p | bus | 869 | -35.76 | 0.04
1000020 | ЮкГрэс 220 | p | bus | 901 | -19.28 | 0.04
1000021 | АТЭЦ-3 110 | p | bus | 905 | 150.48 | 7.524
1000022 | ПС-7 АХБК 110 | p | bus | 913 | 283.46 | 14.173
1000023 | Западная 220 | p | bus | 918 | -43.69 | 0.04
1000024 | Шу 220 | p | bus | 932 | -23.94 | 0.04
1000025 | Мойнакская ГЭС | p | bus | 935 | 129.81 | 6.4905
1000026 | еэк-20-бл5-8 | q | bus | 30 | -0.2 | 0.04
1000027 | эгрэс-1 бл3-2 | q | bus | 50 | 39.74 | 1.987
1000028 | эгрес-1 20 | q | bus | 51 | 123.31 | 6.1655
1000029 | эгрэс-2 20 | q | bus | 60 | 86.43 | 4.3215
1000030 | Таш.ГРЭС | q | bus | 224 | 204 | 10.2
1000031 | Оскаровка 220 | q | bus | 306 | -19.44 | 0.04
1000032 | Нура 220 | q | bus | 310 | -3.22 | 0.04
1000033 | Кар.ГРЭС-2 110 | q | bus | 356 | 1.89 | 0.0945
1000034 | Агадырь 220 | q | bus | 468 | 5.22 | 0.261
1000035 | Агадырь | q | bus | 469 | -40.74 | 0.04
1000036 | ПС 500 кВ Житикара - СШ 500 кВ | q | bus | 577 | 42.72 | 2.136
1000037 | Жамбыл 220 | q | bus | 801 | -103.72 | 0.04
1000038 | Шымкент 220 | q | bus | 831 | -36.44 | 0.04
1000039 | Кентау | q | bus | 840 | -15.13 | 0.04
1000040 | Миргалимсай | q | bus | 842 | -29.11 | 0.04
1000041 | Шымкентская | q | bus | 843 | -116.33 | 0.04
1000042 | Кызылорда 220 | q | bus | 862 | -13.52 | 0.04
1000043 | Ру-6 | q | bus | 869 | 0.81 | 0.0405
1000044 | ЮкГрэс 220 | q | bus | 901 | 0.52 | 0.04
1000045 | АТЭЦ-3 110 | q | bus | 905 | 61.16 | 3.058
1000046 | ПС-7 АХБК 110 | q | bus | 913 | 110.69 | 5.5345
1000047 | Шу 220 | q | bus | 932 | 11.88 | 0.594
1000048 | Алма | q | bus | 938 | -100.14 | 0.04
1000049 | Семей | q | bus | 980 | -132.13 | 0.04
1000050 | Талдыкорган | q | bus | 987 | -160.2 | 0.04
1000051 | ТАВРИЧЕСКАЯ | q | bus | 1817 | -16.51 | 0.04
1000057 | ЦГПП - ПС-ЦГПП 220 - ЦГПП АТ-4 | p | trafo | 6129130 | 260.71 | 13.0355 | 129
1000067 | ЖЕЗКАЗГАН - Жезказган 220 - Жезказган 500 АТ-1 | p | trafo | 16480466 | 146.92 | 7.346 | 480
1000088 | ЦГПП - ПС-ЦГПП 220 - ЦГПП АТ-4 | q | trafo | 6129130 | -70.36 | 0.04 | 129
1000098 | ЖЕЗКАЗГАН - Жезказган 220 - Жезказган 500 АТ-1 | q | trafo | 16480466 | 5.48 | 0.274 | 480
1000114 | ЭГРЭС-1 - ЭГРЭС-1 220 - ЭГРЭС-1 500 АТ | p | trafo | 12539 | -49.14 | 0.04 | 39
1000115 | ЭГРЭС-1 - эгрес-1 20 - ЭГРЭС-1 500 Т3-8 | p | trafo | 22551 | 2222.5 | 111.125 | 51
1000117 | ЕЭК - ПС-ЕЭК 220 - ЕЭК 500 АТ | p | trafo | 43133 | -402.91 | 0.04 | 33
1000118 | ЭГРЭС-1 220 - эгрэс-1 бл3-2 - эгрэс-1 Т1-2 | p | trafo | 53950 | 353.72 | 17.686 | 50
1000119 | ЦГПП - ПС-ЦГПП 220 - ЦГПП АТ-4 | p | trafo | 6129130 | -265.47 | 0.04 | 130
1000122 | Усть-Каменогорск - У-К - У-К 500 АТ-2 | p | trafo | 9240241 | 173.76 | 8.688 | 241
1000123 | Усть-Каменогорск - У-К - У-К 500 АТ-1 | p | trafo | 10240241 | 174.54 | 8.727 | 241
1000124 | Нура - Нура 220 - Нура 500 АТ-1 | p | trafo | 11325310 | -160.85 | 0.04 | 310
1000129 | ЖЕЗКАЗГАН - Жезказган 220 - Жезказган 500 АТ-1 | p | trafo | 16480466 | -146.3 | 0.04 | 466
1000130 | Жамбыл - Жамбыл 220 - Жамбыл АТ-1 | p | trafo | 17800801 | -150.9 | 0.04 | 801
1000131 | Шымкент - Шымкент 220 - Шымкент 500 АТ-1 | p | trafo | 18830831 | -133.61 | 0.04 | 831
1000132 | Шымкент - Шымкент 220 - Шымкент 500 АТ-3 | p | trafo | 19830831 | -108.69 | 0.04 | 831
1000133 | ЮКГРЭС - ЮкГрэс 220 - ЮКГРЭС АТ | p | trafo | 20900901 | -114.15 | 0.04 | 901
1000134 | Алматы - Алматы 220 - Алматы АТ-2 | p | trafo | 21902903 | -108.41 | 0.04 | 903
1000135 | Алматы - Алматы 220 - Алматы АТ-1 | p | trafo | 22902903 | -108.55 | 0.04 | 903
1000138 | Алма - Алма 220 - Алма АТ-2 | p | trafo | 25938939 | -196.75 | 0.04 | 939
1000139 | Алма - Алма 220 - Алма АТ-1 | p | trafo | 26938939 | -197.22 | 0.04 | 939
1000140 | Семей - Семей 220 - Семей 500 АТ-1 | p | trafo | 27980981 | 308.6 | 15.43 | 981
1000141 | Талдыкорган - Талдыкорган 220 - Талдыкорган 500 АТ-1 | p | trafo | 28987988 | -139.99 | 0.04 | 988
1000145 | ЭГРЭС-1 - ЭГРЭС-1 220 - ЭГРЭС-1 500 АТ | q | trafo | 12539 | 127.15 | 6.3575 | 39
1000146 | ЭГРЭС-1 - эгрес-1 20 - ЭГРЭС-1 500 Т3-8 | q | trafo | 22551 | 123.31 | 6.1655 | 51
1000147 | ЕЭК - еэк-20-бл5-8 - ЕЭК 500 Блок 5-8 | q | trafo | 33130 | -0.2 | 0.04 | 30
1000148 | ЕЭК - ПС-ЕЭК 220 - ЕЭК 500 АТ | q | trafo | 43133 | -310.16 | 0.04 | 33
1000149 | ЭГРЭС-1 220 - эгрэс-1 бл3-2 - эгрэс-1 Т1-2 | q | trafo | 53950 | 39.74 | 1.987 | 50
1000150 | ЦГПП - ПС-ЦГПП 220 - ЦГПП АТ-4 | q | trafo | 6129130 | -87.17 | 0.04 | 130
1000153 | Усть-Каменогорск - У-К - У-К 500 АТ-2 | q | trafo | 9240241 | -158.98 | 0.04 | 241
1000154 | Усть-Каменогорск - У-К - У-К 500 АТ-1 | q | trafo | 10240241 | -159.84 | 0.04 | 241
1000155 | Нура - Нура 220 - Нура 500 АТ-1 | q | trafo | 11325310 | 133.11 | 6.6555 | 310
1000160 | ЖЕЗКАЗГАН - Жезказган 220 - Жезказган 500 АТ-1 | q | trafo | 16480466 | -1.17 | 0.04 | 466
1000161 | Жамбыл - Жамбыл 220 - Жамбыл АТ-1 | q | trafo | 17800801 | 17.26 | 0.863 | 801
1000162 | Шымкент - Шымкент 220 - Шымкент 500 АТ-1 | q | trafo | 18830831 | -93 | 0.04 | 831
1000163 | Шымкент - Шымкент 220 - Шымкент 500 АТ-3 | q | trafo | 19830831 | -73.96 | 0.04 | 831
1000164 | ЮКГРЭС - ЮкГрэс 220 - ЮКГРЭС АТ | q | trafo | 20900901 | 52.71 | 2.6355 | 901
1000165 | Алматы - Алматы 220 - Алматы АТ-2 | q | trafo | 21902903 | 6.1 | 0.305 | 903
1000166 | Алматы - Алматы 220 - Алматы АТ-1 | q | trafo | 22902903 | -18.01 | 0.04 | 903
1000169 | Алма - Алма 220 - Алма АТ-2 | q | trafo | 25938939 | 88.14 | 4.407 | 939
1000170 | Алма - Алма 220 - Алма АТ-1 | q | trafo | 26938939 | 88.61 | 4.4305 | 939
1000171 | Семей - Семей 220 - Семей 500 АТ-1 | q | trafo | 27980981 | 19.62 | 0.981 | 981
1000172 | Талдыкорган - Талдыкорган 220 - Талдыкорган 500 АТ-1 | q | trafo | 28987988 | 29.47 | 1.4735 | 988
1000176 | ЭГРЭС-1 - ЕЭК - ВЛ5017 | p | line | 12531 | 296.83 | 14.8415 | 25
1000177 | ЭГРЭС-1 - ЦГПП - ВЛ5050 | p | line | 225129 | 325.69 | 16.2845 | 25
1000178 | ЭГРЭС-1 - Нура - ВЛ5120 | p | line | 325325 | 575.15 | 28.7575 | 25
1000179 | ЭГРЭС-1 - ТАВРИЧЕСКАЯ - ВЛ5577 | p | line | 4251817 | 284.63 | 14.2315 | 25
1000180 | ЭК-1150 - ЭГРЭС-1 - ВЛ5117 | p | line | 52625 | -320.37 | 0.04 | 26
1000181 | ЭК-1150 - ЭГРЭС-1 - ВЛ5107 | p | line | 62625 | -278.44 | 0.04 | 26
1000182 | ЭК-1150 - Кокшетау - ВЛ1101 | p | line | 726175 | 216.74 | 10.837 | 26
1000183 | ЭК-1150 - Агадырь - ВЛ5170 | p | line | 826469 | 578.23 | 28.9115 | 26
1000184 | ЭК-1150 - Алтай - ВЛ1104 | p | line | 9261660 | 66.91 | 3.3455 | 26
1000185 | ЭГРЕС-2 500 - ЭК-1150 - ВЛ5827 | p | line | 102826 | 180.13 | 9.0065 | 28
1000186 | ЭГРЕС-2 500 - ЭК-1150 - ВЛ5817 | p | line | 112826 | 193.98 | 9.699 | 28
1000188 | ЕЭК - Рубцовск - ВЛ5527 | p | line | 13311621 | 30.46 | 1.523 | 31
1000189 | ЕЭК - ИРТЫШСКАЯ - ВЛ5537 | p | line | 14311850 | 240.26 | 12.013 | 31
1000190 | ПС-ЕЭК 220 - пр/уз. ЕЭК Семей - ЭКВ | p | line | 15337202 | 7.95 | 0.3975 | 33
1000191 | ПС-ЕЭК 220 - пр/уз. Эгрэс-1 ЕЭК - ЭКВ | p | line | 16337203 | 63.27 | 3.1635 | 33
1000192 | ЭГРЭС-1 220 - пр/уз. Эгрэс-1 ЕЭК - ЭКВ | p | line | 17397203 | 43.72 | 2.186 | 39
1000193 | ЭГРЭС-1 220 - пр/уз.ЦГПП-ЭГРЭС-1 - ЭКВ | p | line | 18397204 | 72.24 | 3.612 | 39
1000194 | ЭГРЭС-1 220 - пр/уз.ЭГРЭС 1 Осакоровка - ЭКВ | p | line | 19397206 | 89.35 | 4.4675 | 39
1000195 | ЦГПП - ПС-ЕГПП - ВЛ5071 | p | line | 20129180 | 68.82 | 3.441 | 129
1000196 | ПС-ЦГПП 220 - пр/уз.ЦГПП-ЭГРЭС-1 - ЭКВ | p | line | 211307204 | -56.38 | 0.04 | 130
1000197 | ПС-ЦГПП 220 - пр/уз.ЦГПП-Осакоровка - ЭКВ | p | line | 221307205 | 64.95 | 3.2475 | 130
1000198 | АВРОРА 500 - ТАВРИЧЕСКАЯ - ВЛ5561 | p | line | 231471817 | -47.46 | 0.04 | 147
1000201 | Кокшетау - Костанай - ВЛ1102 | p | line | 26175590 | 15.03 | 0.7515 | 175
1000202 | ПС-ЕГПП - Сокол - ВЛ5086 | p | line | 27180576 | -3.16 | 0.04 | 180
1000203 | Таш.ГРЭС - Ташкент - ВЛ522 | p | line | 2822463 | 2934 | 146.7 | 224
1000204 | Таш.ГРЭС - Шымкент - ВЛ5019 | p | line | 29224830 | 471.1 | 23.555 | 224
1000205 | У-К - пр/уз. Семей У-К - ЭКВ | p | line | 302417201 | -148.62 | 0.04 | 241
1000206 | Оскаровка 220 - пр/уз.ЦГПП-Осакоровка - ЭКВ | p | line | 313067205 | -60.3 | 0.04 | 306
1000207 | Оскаровка 220 - пр/уз.ЭГРЭС 1 Осакоровка - ЭКВ | p | line | 323067206 | -60.39 | 0.04 | 306
1000208 | Оскаровка 220 - пр/уз.Кар.ГРЭС-2 Осакоровка - экв_ВЛ2258_ВЛ2268 | p | line | 333067229 | 98.8 | 4.94 | 306
1000209 | Нура 220 - пр/уз.КарГРЭС-Нура - ЭКВ | p | line | 343107208 | 129.13 | 6.4565 | 310
1000210 | Нура - Агадырь - ВЛ5138 | p | line | 35325469 | 419.22 | 20.961 | 325
1000211 | Кар.ГРЭС-2 - пр/уз.КарГРЭС-Нура - ЭКВ | p | line | 363557208 | -85.18 | 0.04 | 355
1000212 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Каражал - ЭКВ | p | line | 373557209 | 61.16 | 3.058 | 355
1000213 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Агадырь - ЭКВ | p | line | 383557210 | 56.76 | 2.838 | 355
1000214 | Кар.ГРЭС-2 - пр/уз.Каргрэс - Балхашская - ЭКВ | p | line | 393557211 | 56.23 | 2.8115 | 355
1000215 | Кар.ГРЭС-2 - пр/уз.Кар.ГРЭС-2 Осакоровка - экв_ВЛ2258_ВЛ2268 | p | line | 403557229 | -54.08 | 0.04 | 355
1000216 | Каражал 220 - Агадырь - ВЛ2428 | p | line | 41465468 | -33.24 | 0.04 | 465
1000217 | Каражал 220 - пр/уз.Каргрэс-Каражал - ЭКВ | p | line | 424657209 | -53.42 | 0.04 | 465
1000218 | Каражал 220 - пр/уз ЖезказганКаражал - ЭКВ | p | line | 434657221 | 79.66 | 3.983 | 465
1000219 | Жезказган 220 - Кумколь 220 - ЭКВ_2318_2328 | p | line | 44466467 | 49.25 | 2.4625 | 466
1000220 | Жезказган 220 - пр/уз ЖезказганКаражал - ЭКВ | p | line | 454667221 | 97.46 | 4.873 | 466
1000221 | Кумколь 220 - пр/уз Кызылорда-Кумколь - ЭКВ | p | line | 464677227 | 68.29 | 3.4145 | 467
1000223 | Агадырь 220 - пр/уз.Каргрэс-Агадырь - ЭКВ | p | line | 484687210 | -35.15 | 0.04 | 468
1000224 | Агадырь - ЖЕЗКАЗГАН - ВЛ5148 | p | line | 49469480 | 148.71 | 7.4355 | 469
1000225 | Агадырь - ЮКГРЭС - ВЛ5300 | p | line | 50469900 | 409.48 | 20.474 | 469
1000226 | Агадырь - ЮКГРЭС - ВЛ5320 | p | line | 51469900 | 413.44 | 20.672 | 469
1000227 | Балхашская - Мойынты - ВЛ2448 | p | line | 52473475 | -33.62 | 0.04 | 473
1000228 | Балхашская - пр/уз.Каргрэс - Балхашская - ЭКВ | p | line | 534737211 | -42.08 | 0.04 | 473
1000231 | Л-5726 (Сокол - Житикара) | p | line | 56576577 | 197.76 | 9.888 | 576
1000232 | Костанай - Сокол - ВЛ5096 | p | line | 57590576 | 396.31 | 19.8155 | 590
1000233 | Л-1103 (Костанайская - Челябинская) | p | line | 585904705 | -514.17 | 0.04 | 590
1000234 | Жамбыл - Шымкент - ВЛ5169 | p | line | 59800830 | -210.94 | 0.04 | 800
1000235 | Жамбыл 220 - жгрэс-220 - ЭКВ_Жамбыл_ЖГРЭС | p | line | 60801805 | -9.92 | 0.04 | 801
1000236 | Жамбыл 220 - пр/уз Жамбыл Шымкент - ЭКВ | p | line | 618017216 | -66.65 | 0.04 | 801
1000238 | Шымкент 220 - Шымкентская - ВЛ2349 | p | line | 63831843 | 49.42 | 2.471 | 831
1000239 | Шымкент 220 - пр/уз Жамбыл Шымкент - ЭКВ | p | line | 648317216 | 92.76 | 4.638 | 831
1000240 | Шымкент 220 - Пр/уз Шымкент-220/Жылга - ЭКВ | p | line | 658317225 | -23.15 | 0.04 | 831
1000241 | Шымкент 220 - ГНПС - ВЛ2309 | p | line | 668317228 | -4.52 | 0.04 | 831
1000245 | Кентау - Ру-6 - ВЛ2519 | p | line | 70840869 | 8.25 | 0.4125 | 840
1000246 | Кентау - пр/уз Кентау Жамбыл 220 - ЭКВ | p | line | 718407224 | -17.96 | 0.04 | 840
1000247 | Миргалимсай - Кентау - ВЛ2549 | p | line | 72842840 | 14.65 | 0.7325 | 842
1000248 | Миргалимсай - Шымкентская - ВЛ2319 | p | line | 73842843 | -38.24 | 0.04 | 842
1000249 | Кызылорда 220 - пр/уз Ру-6/Кызылорда - ЭКВ | p | line | 748627226 | 16.6 | 0.83 | 862
1000250 | Кызылорда 220 - пр/уз Кызылорда-Кумколь - ЭКВ | p | line | 758627227 | -35.29 | 0.04 | 862
1000251 | Жанакорган - Миргалимсай - ВЛ2539 | p | line | 76865842 | -8.4 | 0.04 | 865
1000252 | Жанакорган - Ру-6 - ВЛ2529 | p | line | 77865869 | 8.1 | 0.405 | 865
1000253 | Ру-6 - пр/уз Ру-6/Кызылорда - ЭКВ | p | line | 788697226 | -20.18 | 0.04 | 869
1000254 | ЮКГРЭС - Алматы - ВЛ5313 | p | line | 79900902 | 236.29 | 11.8145 | 900
1000255 | ЮКГРЭС - Алма - ВЛ5363 | p | line | 80900938 | 86.82 | 4.341 | 900
1000256 | ЮКГРЭС - ЧУ - ВЛ5333 | p | line | 819009932 | 348.66 | 17.433 | 900
1000257 | ЮкГрэс 220 - пр/уз ЮкГРЭС ШУ - ЭКВ | p | line | 829017212 | 81.97 | 4.0985 | 901
1000258 | ЮкГрэс 220 - пр/уз МойынтыЮкгрэс - ЭКВ | p | line | 839017219 | 11.14 | 0.557 | 901
1000260 | Алматы - ЧУ - ВЛ5343 | p | line | 859029932 | 22.79 | 1.1395 | 902
1000261 | Алматы 220 - АТЭЦ-3 - ВЛ2013 | p | line | 86903904 | 13.75 | 0.6875 | 903
1000262 | Алматы 220 - Робот - ВЛ2053 | p | line | 87903907 | -64.22 | 0.04 | 903
1000263 | Алматы 220 - Медео - ВЛ2773 | p | line | 88903928 | 12.88 | 0.644 | 903
1000264 | Алматы 220 - пр/уз Алматы Алма - ЭКВ | p | line | 899037213 | 117.82 | 5.891 | 903
1000265 | АТЭЦ-3 - Алма 220 - ВЛ2113 и ВЛ2103 | p | line | 90904939 | -278 | 0.04 | 904
1000266 | Робот - пр/уз ТалдыкорганРобот - ЭКВ | p | line | 919077218 | -92.9 | 0.04 | 907
1000267 | ПС-7 АХБК - Коян-Кос - ЭКВ | p | line | 92912953 | -176.22 | 0.04 | 912
1000268 | Западная 220 - ПС-7 АХБК - ВЛ2173 | p | line | 93918912 | -50.33 | 0.04 | 918
1000269 | Западная 220 - Кемин 220 - ВЛ2183 | p | line | 949182952 | 68.89 | 3.4445 | 918
1000271 | Шу 220 - Аспара - ВЛ2233 | p | line | 96932814 | -15.66 | 0.04 | 932
1000272 | Шу 220 - Главная 220 - ВЛ2163 | p | line | 979321916 | 84.58 | 4.229 | 932
1000273 | Шу 220 - пр/уз ЮкГРЭС ШУ - ЭКВ | p | line | 989327212 | -62.65 | 0.04 | 932
1000274 | Мойнакская ГЭС - Робот | p | line | 99935907 | 46.22 | 2.311 | 935
1000275 | Мойнакская ГЭС - Чилик | p | line | 100935911 | 83.58 | 4.179 | 935
1000276 | Алма 220 - Робот - ВЛ2463 | p | line | 101939907 | -55.99 | 0.04 | 939
1000278 | Алма 220 - пр/уз Алматы Алма - ЭКВ | p | line | 1039397213 | 217.59 | 10.8795 | 939
1000280 | Семей - ЭК-1150 - ВЛ5370 | p | line | 10598026 | -93.66 | 0.04 | 980
1000281 | Семей - Усть-Каменогорск - ВЛ5384 | p | line | 106980240 | -145.84 | 0.04 | 980
1000282 | Семей - Актогай - ВЛ5394 | p | line | 107980986 | 543.82 | 27.191 | 980
1000283 | Семей 220 - пр/уз. Семей У-К - ЭКВ | p | line | 1089817201 | -433.71 | 0.04 | 981
1000284 | Семей 220 - пр/уз. ЕЭК Семей - ЭКВ | p | line | 1099817202 | 9.57 | 0.4785 | 981
1000285 | Актогай - Талдыкорган - ВЛ5400 | p | line | 110986987 | 462.8 | 23.14 | 986
1000286 | Талдыкорган - Алма - ВЛ5413 | p | line | 111987938 | 310.06 | 15.503 | 987
1000287 | Талдыкорган 220 - пр/уз ТалдыкорганРобот - ЭКВ | p | line | 1129887218 | 94.56 | 4.728 | 988
1000288 | Рубцовск - Усть-Каменогорск - ВЛ5544 | p | line | 1131621240 | -202.28 | 0.04 | 1621
1000289 | Барнаул - Рубцовск - ВЛ551 | p | line | 11416301621 | 28.53 | 1.4265 | 1630
1000291 | Алтай - Барнаул - ВЛ596 | p | line | 11616601630 | -158.72 | 0.04 | 1660
1000292 | Алтай - Барнаул - ВЛ595 | p | line | 11716601630 | -110.96 | 0.04 | 1660
1000295 | ТАВРИЧЕСКАЯ - ИРТЫШСКАЯ - ВЛ555 | p | line | 12018171850 | 30.26 | 1.513 | 1817
1000299 | Главная 220 - Алматы 220 - ВЛ2193 | p | line | 1241916903 | -112.68 | 0.04 | 1916
1000300 | Главная 220 - пр/уз Главная Кемин - ЭКВ | p | line | 12519167214 | 0.1 | 0.04 | 1916
1000301 | Главная 220 - пр/уз ГлавнаяФрунзе - ЭКВ | p | line | 12619167217 | -70.2 | 0.04 | 1916
1000304 | Фрунзе - Жамбыл - ВЛ5159 | p | line | 1292919800 | -69.42 | 0.04 | 2919
1000305 | Фрунзе - ГЕНЕРАЦИЯ ЦА-1 - ЭКВ_509 | p | line | 13029192921 | 27.72 | 1.386 | 2919
1000306 | ТашкентТэс 220 - Шымкентская - ВЛ2419 | p | line | 1312925843 | 103.63 | 5.1815 | 2925
1000307 | Кемин 220 - пр/уз Главная Кемин - ЭКВ | p | line | 13229527214 | -41.63 | 0.04 | 2952
1000322 | ЧУ - Фрунзе - ВЛ5143 | p | line | 14799322919 | 371.78 | 18.589 | 9932
1000324 | ЭГРЭС-1 - ЕЭК - ВЛ5017 | q | line | 12531 | 13.48 | 0.674 | 25
1000325 | ЭГРЭС-1 - ЦГПП - ВЛ5050 | q | line | 225129 | -154.58 | 0.04 | 25
1000326 | ЭГРЭС-1 - Нура - ВЛ5120 | q | line | 325325 | -151.88 | 0.04 | 25
1000327 | ЭГРЭС-1 - ТАВРИЧЕСКАЯ - ВЛ5577 | q | line | 4251817 | -194.8 | 0.04 | 25
1000328 | ЭК-1150 - ЭГРЭС-1 - ВЛ5117 | q | line | 52625 | -0.79 | 0.04 | 26
1000329 | ЭК-1150 - ЭГРЭС-1 - ВЛ5107 | q | line | 62625 | -7.91 | 0.04 | 26
1000330 | ЭК-1150 - Кокшетау - ВЛ1101 | q | line | 726175 | -67.24 | 0.04 | 26
1000331 | ЭК-1150 - Агадырь - ВЛ5170 | q | line | 826469 | -179 | 0.04 | 26
1000332 | ЭК-1150 - Алтай - ВЛ1104 | q | line | 9261660 | -337.36 | 0.04 | 26
1000336 | ЕЭК - Рубцовск - ВЛ5527 | q | line | 13311621 | -223.34 | 0.04 | 31
1000337 | ЕЭК - ИРТЫШСКАЯ - ВЛ5537 | q | line | 14311850 | -120.98 | 0.04 | 31
1000338 | ПС-ЕЭК 220 - пр/уз. ЕЭК Семей - ЭКВ | q | line | 15337202 | -22.01 | 0.04 | 33
1000339 | ПС-ЕЭК 220 - пр/уз. Эгрэс-1 ЕЭК - ЭКВ | q | line | 16337203 | -30.16 | 0.04 | 33
1000340 | ЭГРЭС-1 220 - пр/уз. Эгрэс-1 ЕЭК - ЭКВ | q | line | 17397203 | 5.7 | 0.285 | 39
1000341 | ЭГРЭС-1 220 - пр/уз.ЦГПП-ЭГРЭС-1 - ЭКВ | q | line | 18397204 | -72.24 | 0.04 | 39
1000342 | ЭГРЭС-1 220 - пр/уз.ЭГРЭС 1 Осакоровка - ЭКВ | q | line | 19397206 | -43.72 | 0.04 | 39
1000343 | ЦГПП - ПС-ЕГПП - ВЛ5071 | q | line | 20129180 | 8.7 | 0.435 | 129
1000344 | ПС-ЦГПП 220 - пр/уз.ЦГПП-ЭГРЭС-1 - ЭКВ | q | line | 211307204 | 22.76 | 1.138 | 130
1000345 | ПС-ЦГПП 220 - пр/уз.ЦГПП-Осакоровка - ЭКВ | q | line | 221307205 | -59.1 | 0.04 | 130
1000346 | АВРОРА 500 - ТАВРИЧЕСКАЯ - ВЛ5561 | q | line | 231471817 | -134.48 | 0.04 | 147
1000349 | Кокшетау - Костанай - ВЛ1102 | q | line | 26175590 | -132.1 | 0.04 | 175
1000350 | ПС-ЕГПП - Сокол - ВЛ5086 | q | line | 27180576 | -19.78 | 0.04 | 180
1000351 | Таш.ГРЭС - Ташкент - ВЛ522 | q | line | 2822463 | 204 | 10.2 | 224
1000353 | У-К - пр/уз. Семей У-К - ЭКВ | q | line | 302417201 | 35.15 | 1.7575 | 241
1000354 | Оскаровка 220 - пр/уз.ЦГПП-Осакоровка - ЭКВ | q | line | 313067205 | -26.1 | 0.04 | 306
1000355 | Оскаровка 220 - пр/уз.ЭГРЭС 1 Осакоровка - ЭКВ | q | line | 323067206 | 10.57 | 0.5285 | 306
1000356 | Оскаровка 220 - пр/уз.Кар.ГРЭС-2 Осакоровка - экв_ВЛ2258_ВЛ2268 | q | line | 333067229 | 10.44 | 0.522 | 306
1000357 | Нура 220 - пр/уз.КарГРЭС-Нура - ЭКВ | q | line | 343107208 | 129.3 | 6.465 | 310
1000358 | Нура - Агадырь - ВЛ5138 | q | line | 35325469 | -105.6 | 0.04 | 325
1000359 | Кар.ГРЭС-2 - пр/уз.КарГРЭС-Нура - ЭКВ | q | line | 363557208 | 43.82 | 2.191 | 355
1000360 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Каражал - ЭКВ | q | line | 373557209 | -46.46 | 0.04 | 355
1000361 | Кар.ГРЭС-2 - пр/уз.Каргрэс-Агадырь - ЭКВ | q | line | 383557210 | -46.42 | 0.04 | 355
1000362 | Кар.ГРЭС-2 - пр/уз.Каргрэс - Балхашская - ЭКВ | q | line | 393557211 | -39.47 | 0.04 | 355
1000363 | Кар.ГРЭС-2 - пр/уз.Кар.ГРЭС-2 Осакоровка - экв_ВЛ2258_ВЛ2268 | q | line | 403557229 | -28.07 | 0.04 | 355
1000367 | Жезказган 220 - Кумколь 220 - ЭКВ_2318_2328 | q | line | 44466467 | -41.77 | 0.04 | 466
1000368 | Жезказган 220 - пр/уз ЖезказганКаражал - ЭКВ | q | line | 454667221 | 42.81 | 2.1405 | 466
1000369 | Кумколь 220 - пр/уз Кызылорда-Кумколь - ЭКВ | q | line | 464677227 | -23.28 | 0.04 | 467
1000371 | Агадырь 220 - пр/уз.Каргрэс-Агадырь - ЭКВ | q | line | 484687210 | 32.89 | 1.6445 | 468
1000372 | Агадырь - ЖЕЗКАЗГАН - ВЛ5148 | q | line | 49469480 | -241.27 | 0.04 | 469
1000373 | Агадырь - ЮКГРЭС - ВЛ5300 | q | line | 50469900 | -213.58 | 0.04 | 469
1000374 | Агадырь - ЮКГРЭС - ВЛ5320 | q | line | 51469900 | -207.39 | 0.04 | 469
1000375 | Балхашская - Мойынты - ВЛ2448 | q | line | 52473475 | -51.69 | 0.04 | 473
1000376 | Балхашская - пр/уз.Каргрэс - Балхашская - ЭКВ | q | line | 534737211 | 18.17 | 0.9085 | 473
1000379 | Л-5726 (Сокол - Житикара) | q | line | 56576577 | -15.82 | 0.04 | 576
1000380 | Костанай - Сокол - ВЛ5096 | q | line | 57590576 | -113.91 | 0.04 | 590
1000381 | Л-1103 (Костанайская - Челябинская) | q | line | 585904705 | -95.72 | 0.04 | 590
1000382 | Жамбыл - Шымкент - ВЛ5169 | q | line | 59800830 | -11.38 | 0.04 | 800
1000383 | Жамбыл 220 - жгрэс-220 - ЭКВ_Жамбыл_ЖГРЭС | q | line | 60801805 | -27.32 | 0.04 | 801
1000384 | Жамбыл 220 - пр/уз Жамбыл Шымкент - ЭКВ | q | line | 618017216 | -26.45 | 0.04 | 801
1000386 | Шымкент 220 - Шымкентская - ВЛ2349 | q | line | 63831843 | 114.86 | 5.743 | 831
1000387 | Шымкент 220 - пр/уз Жамбыл Шымкент - ЭКВ | q | line | 648317216 | 6.61 | 0.3305 | 831
1000388 | Шымкент 220 - Пр/уз Шымкент-220/Жылга - ЭКВ | q | line | 658317225 | 12.0079 | 0.6004 | 831
1000389 | Шымкент 220 - ГНПС - ВЛ2309 | q | line | 668317228 | -6.61 | 0.04 | 831
1000393 | Кентау - Ру-6 - ВЛ2519 | q | line | 70840869 | -20.36 | 0.04 | 840
1000394 | Кентау - пр/уз Кентау Жамбыл 220 - ЭКВ | q | line | 718407224 | -9.08 | 0.04 | 840
1000395 | Миргалимсай - Кентау - ВЛ2549 | q | line | 72842840 | -16.35 | 0.04 | 842
1000396 | Миргалимсай - Шымкентская - ВЛ2319 | q | line | 73842843 | 5.53 | 0.2765 | 842
1000397 | Кызылорда 220 - пр/уз Ру-6/Кызылорда - ЭКВ | q | line | 748627226 | -29.97 | 0.04 | 862
1000398 | Кызылорда 220 - пр/уз Кызылорда-Кумколь - ЭКВ | q | line | 758627227 | -4.39 | 0.04 | 862
1000399 | Жанакорган - Миргалимсай - ВЛ2539 | q | line | 76865842 | 1.92 | 0.096 | 865
1000400 | Жанакорган - Ру-6 - ВЛ2529 | q | line | 77865869 | -7.07 | 0.04 | 865
1000401 | Ру-6 - пр/уз Ру-6/Кызылорда - ЭКВ | q | line | 788697226 | 8.86 | 0.443 | 869
1000402 | ЮКГРЭС - Алматы - ВЛ5313 | q | line | 79900902 | -163.64 | 0.04 | 900
1000403 | ЮКГРЭС - Алма - ВЛ5363 | q | line | 80900938 | -210.62 | 0.04 | 900
1000404 | ЮКГРЭС - ЧУ - ВЛ5333 | q | line | 819009932 | -65.3 | 0.04 | 900
1000405 | ЮкГрэс 220 - пр/уз ЮкГРЭС ШУ - ЭКВ | q | line | 829017212 | -21.23 | 0.04 | 901
1000406 | ЮкГрэс 220 - пр/уз МойынтыЮкгрэс - ЭКВ | q | line | 839017219 | -29.93 | 0.04 | 901
1000408 | Алматы - ЧУ - ВЛ5343 | q | line | 859029932 | -73.57 | 0.04 | 902
1000409 | Алматы 220 - АТЭЦ-3 - ВЛ2013 | q | line | 86903904 | 33.94 | 1.697 | 903
1000410 | Алматы 220 - Робот - ВЛ2053 | q | line | 87903907 | 9.22 | 0.461 | 903
1000411 | Алматы 220 - Медео - ВЛ2773 | q | line | 88903928 | 31.5 | 1.575 | 903
1000412 | Алматы 220 - пр/уз Алматы Алма - ЭКВ | q | line | 899037213 | -72.22 | 0.04 | 903
1000413 | АТЭЦ-3 - Алма 220 - ВЛ2113 и ВЛ2103 | q | line | 90904939 | -37.03 | 0.04 | 904
1000414 | Робот - пр/уз ТалдыкорганРобот - ЭКВ | q | line | 919077218 | -11 | 0.04 | 907
1000415 | ПС-7 АХБК - Коян-Кос - ЭКВ | q | line | 92912953 | -39.96 | 0.04 | 912
1000416 | Западная 220 - ПС-7 АХБК - ВЛ2173 | q | line | 93918912 | -50.33 | 0.04 | 918
1000417 | Западная 220 - Кемин 220 - ВЛ2183 | q | line | 949182952 | 28.58 | 1.429 | 918
1000419 | Шу 220 - Аспара - ВЛ2233 | q | line | 96932814 | -6.09 | 0.04 | 932
1000420 | Шу 220 - Главная 220 - ВЛ2163 | q | line | 979321916 | 36.02 | 1.801 | 932
1000421 | Шу 220 - пр/уз ЮкГРЭС ШУ - ЭКВ | q | line | 989327212 | -2.96 | 0.04 | 932
1000422 | Мойнакская ГЭС - Робот | q | line | 99935907 | -8.86 | 0.04 | 935
1000423 | Мойнакская ГЭС - Чилик | q | line | 100935911 | 11.3 | 0.565 | 935
1000424 | Алма 220 - Робот - ВЛ2463 | q | line | 101939907 | -52.92 | 0.04 | 939
1000426 | Алма 220 - пр/уз Алматы Алма - ЭКВ | q | line | 1039397213 | -138.76 | 0.04 | 939
1000428 | Семей - ЭК-1150 - ВЛ5370 | q | line | 10598026 | -216.88 | 0.04 | 980
1000429 | Семей - Усть-Каменогорск - ВЛ5384 | q | line | 106980240 | -50.09 | 0.04 | 980
1000430 | Семей - Актогай - ВЛ5394 | q | line | 107980986 | -201.17 | 0.04 | 980
1000431 | Семей 220 - пр/уз. Семей У-К - ЭКВ | q | line | 1089817201 | 7.48 | 0.374 | 981
1000432 | Семей 220 - пр/уз. ЕЭК Семей - ЭКВ | q | line | 1099817202 | -55.32 | 0.04 | 981
1000433 | Актогай - Талдыкорган - ВЛ5400 | q | line | 110986987 | -124.58 | 0.04 | 986
1000434 | Талдыкорган - Алма - ВЛ5413 | q | line | 111987938 | -197.39 | 0.04 | 987
1000435 | Талдыкорган 220 - пр/уз ТалдыкорганРобот - ЭКВ | q | line | 1129887218 | -45.44 | 0.04 | 988
1000436 | Рубцовск - Усть-Каменогорск - ВЛ5544 | q | line | 1131621240 | -57.24 | 0.04 | 1621
1000437 | Барнаул - Рубцовск - ВЛ551 | q | line | 11416301621 | -39.94 | 0.04 | 1630
1000439 | Алтай - Барнаул - ВЛ596 | q | line | 11616601630 | 103.77 | 5.1885 | 1660
1000440 | Алтай - Барнаул - ВЛ595 | q | line | 11716601630 | 60.23 | 3.0115 | 1660
1000443 | ТАВРИЧЕСКАЯ - ИРТЫШСКАЯ - ВЛ555 | q | line | 12018171850 | 37.88 | 1.894 | 1817
1000448 | Главная 220 - пр/уз Главная Кемин - ЭКВ | q | line | 12519167214 | 0.1 | 0.04 | 1916
1000449 | Главная 220 - пр/уз ГлавнаяФрунзе - ЭКВ | q | line | 12619167217 | 18.19 | 0.9095 | 1916
1000454 | ТашкентТэс 220 - Шымкентская - ВЛ2419 | q | line | 1312925843 | 45.72 | 2.286 | 2925
1000470 | ЧУ - Фрунзе - ВЛ5143 | q | line | 14799322919 | -40.48 | 0.04 | 9932
1000472 | ЭГРЭС-1 - ЕЭК - ВЛ5017 | p | line | 12531 | -296.95 | 0.04 | 31
1000473 | ЭГРЭС-1 - ЦГПП - ВЛ5050 | p | line | 225129 | -328.28 | 0.04 | 129
1000474 | ЭГРЭС-1 - Нура - ВЛ5120 | p | line | 325325 | -569 | 0.04 | 325
1000475 | ЭГРЭС-1 - ТАВРИЧЕСКАЯ - ВЛ5577 | p | line | 4251817 | -274.6 | 0.04 | 1817
1000476 | ЭК-1150 - ЭГРЭС-1 - ВЛ5117 | p | line | 52625 | 318.11 | 15.9055 | 25
1000477 | ЭК-1150 - ЭГРЭС-1 - ВЛ5107 | p | line | 62625 | 272.82 | 13.641 | 25
1000478 | ЭК-1150 - Кокшетау - ВЛ1101 | p | line | 726175 | -215.95 | 0.04 | 175
1000479 | ЭК-1150 - Агадырь - ВЛ5170 | p | line | 826469 | -552.26 | 0.04 | 469
1000480 | ЭК-1150 - Алтай - ВЛ1104 | p | line | 9261660 | -68.27 | 0.04 | 1660
1000481 | ЭГРЕС-2 500 - ЭК-1150 - ВЛ5827 | p | line | 102826 | -185.89 | 0.04 | 26
1000482 | ЭГРЕС-2 500 - ЭК-1150 - ВЛ5817 | p | line | 112826 | -193.8 | 0.04 | 26
1000484 | ЕЭК - Рубцовск - ВЛ5527 | p | line | 13311621 | 22.64 | 1.132 | 1621
1000485 | ЕЭК - ИРТЫШСКАЯ - ВЛ5537 | p | line | 14311850 | -237.36 | 0.04 | 1850
1000491 | ЦГПП - ПС-ЕГПП - ВЛ5071 | p | line | 20129180 | -75.15 | 0.04 | 180
1000494 | АВРОРА 500 - ТАВРИЧЕСКАЯ - ВЛ5561 | p | line | 231471817 | -47.74 | 0.04 | 1817
1000497 | Кокшетау - Костанай - ВЛ1102 | p | line | 26175590 | -16.61 | 0.04 | 590
1000498 | ПС-ЕГПП - Сокол - ВЛ5086 | p | line | 27180576 | -2.37 | 0.04 | 576
1000500 | Таш.ГРЭС - Шымкент - ВЛ5019 | p | line | 29224830 | -456.6 | 0.04 | 830
1000506 | Нура - Агадырь - ВЛ5138 | p | line | 35325469 | -417.12 | 0.04 | 469
1000515 | Жезказган 220 - Кумколь 220 - ЭКВ_2318_2328 | p | line | 44466467 | -48.34 | 0.04 | 467
1000520 | Агадырь - ЖЕЗКАЗГАН - ВЛ5148 | p | line | 49469480 | -145.55 | 0.04 | 480
1000521 | Агадырь - ЮКГРЭС - ВЛ5300 | p | line | 50469900 | -404.79 | 0.04 | 900
1000522 | Агадырь - ЮКГРЭС - ВЛ5320 | p | line | 51469900 | -404.79 | 0.04 | 900
1000525 | Мойынты - Агадырь 220 - ВЛ2438 | p | line | 54475468 | 45.94 | 2.297 | 468
1000528 | Костанай - Сокол - ВЛ5096 | p | line | 57590576 | -397.89 | 0.04 | 576
1000530 | Жамбыл - Шымкент - ВЛ5169 | p | line | 59800830 | 210.09 | 10.5045 | 830
1000531 | Жамбыл 220 - жгрэс-220 - ЭКВ_Жамбыл_ЖГРЭС | p | line | 60801805 | 11.11 | 0.5555 | 805
1000533 | Аспара - жгрэс-220 - ВЛ2249 | p | line | 62814805 | 15.66 | 0.783 | 805
1000534 | Шымкент 220 - Шымкентская - ВЛ2349 | p | line | 63831843 | -46.99 | 0.04 | 843
1000538 | Жылга - Шымкентская - ВЛ2449 | p | line | 67839843 | -66.83 | 0.04 | 843
1000539 | Жылга - ТашкентТэс 220 - ВЛ2429 | p | line | 688392925 | 100.58 | 5.029 | 2925
1000541 | Кентау - Ру-6 - ВЛ2519 | p | line | 70840869 | -8.68 | 0.04 | 869
1000543 | Миргалимсай - Кентау - ВЛ2549 | p | line | 72842840 | -17.33 | 0.04 | 840
1000544 | Миргалимсай - Шымкентская - ВЛ2319 | p | line | 73842843 | 40.93 | 2.0465 | 843
1000547 | Жанакорган - Миргалимсай - ВЛ2539 | p | line | 76865842 | 7.35 | 0.3675 | 842
1000548 | Жанакорган - Ру-6 - ВЛ2529 | p | line | 77865869 | -7.61 | 0.04 | 869
1000550 | ЮКГРЭС - Алматы - ВЛ5313 | p | line | 79900902 | -241.04 | 0.04 | 902
1000551 | ЮКГРЭС - Алма - ВЛ5363 | p | line | 80900938 | -93.57 | 0.04 | 938
1000552 | ЮКГРЭС - ЧУ - ВЛ5333 | p | line | 819009932 | -351.92 | 0.04 | 9932
1000556 | Алматы - ЧУ - ВЛ5343 | p | line | 859029932 | -31.77 | 0.04 | 9932
1000557 | Алматы 220 - АТЭЦ-3 - ВЛ2013 | p | line | 86903904 | -13.3 | 0.04 | 904
1000558 | Алматы 220 - Робот - ВЛ2053 | p | line | 87903907 | 65.7 | 3.285 | 907
1000561 | АТЭЦ-3 - Алма 220 - ВЛ2113 и ВЛ2103 | p | line | 90904939 | 278.25 | 13.9125 | 939
1000564 | Западная 220 - ПС-7 АХБК - ВЛ2173 | p | line | 93918912 | 112.57 | 5.6285 | 912
1000565 | Западная 220 - Кемин 220 - ВЛ2183 | p | line | 949182952 | -62.62 | 0.04 | 2952
1000566 | Медео - АТЭЦ-3 - ВЛ2023 | p | line | 95928904 | -5.68 | 0.04 | 904
1000568 | Шу 220 - Главная 220 - ВЛ2163 | p | line | 979321916 | -82.2 | 0.04 | 1916
1000570 | Мойнакская ГЭС - Робот | p | line | 99935907 | -45.2 | 0.04 | 907
1000572 | Алма 220 - Робот - ВЛ2463 | p | line | 101939907 | 55.7 | 2.785 | 907
1000575 | Коян-Кос - АТЭЦ-3 - ЭКВ | p | line | 104953904 | 184.72 | 9.236 | 904
1000576 | Семей - ЭК-1150 - ВЛ5370 | p | line | 10598026 | 96.0023 | 4.8001 | 26
1000577 | Семей - Усть-Каменогорск - ВЛ5384 | p | line | 106980240 | 142.84 | 7.142 | 240
1000578 | Семей - Актогай - ВЛ5394 | p | line | 107980986 | -535.76 | 0.04 | 986
1000581 | Актогай - Талдыкорган - ВЛ5400 | p | line | 110986987 | -460.14 | 0.04 | 987
1000582 | Талдыкорган - Алма - ВЛ5413 | p | line | 111987938 | -311.08 | 0.04 | 938
1000584 | Рубцовск - Усть-Каменогорск - ВЛ5544 | p | line | 1131621240 | 198.24 | 9.912 | 240
1000585 | Барнаул - Рубцовск - ВЛ551 | p | line | 11416301621 | 36.82 | 1.841 | 1621
1000587 | Алтай - Барнаул - ВЛ596 | p | line | 11616601630 | -155.97 | 0.04 | 1630
1000588 | Алтай - Барнаул - ВЛ595 | p | line | 11716601630 | 109.48 | 5.474 | 1630
1000591 | ТАВРИЧЕСКАЯ - ИРТЫШСКАЯ - ВЛ555 | p | line | 12018171850 | -27.51 | 0.04 | 1850
1000595 | Главная 220 - Алматы 220 - ВЛ2193 | p | line | 1241916903 | 112.07 | 5.6035 | 903
1000600 | Фрунзе - Жамбыл - ВЛ5159 | p | line | 1292919800 | 53.43 | 2.6715 | 800
1000602 | ТашкентТэс 220 - Шымкентская - ВЛ2419 | p | line | 1312925843 | -104.42 | 0.04 | 843
1000611 | Л-5736 (Ириклинская ГРЭС -Житикара) | p | line | 1404790577 | -81.48 | 0.04 | 577
1000613 | Л-5716 (Троицкая ГРЭС - Сокол) | p | line | 1424799576 | 88.6 | 4.43 | 576
1000614 | пр/уз жгрэс- Фрунзе - жгрэс-220 - ЭКВ | p | line | 1437223805 | 24.71 | 1.2355 | 805
1000615 | пр/уз жгрэс- Фрунзе - Фрунзе 220 - ЭКВ | p | line | 14472232918 | -15.14 | 0.04 | 2918
1000616 | пр/уз Кентау Жамбыл 220 - Жамбыл 220 - ЭКВ | p | line | 1457224801 | 26.45 | 1.3225 | 801
1000618 | ЧУ - Фрунзе - ВЛ5143 | p | line | 14799322919 | -374 | 0.04 | 2919
1000620 | ЭГРЭС-1 - ЕЭК - ВЛ5017 | q | line | 12531 | -126.05 | 0.04 | 31
1000621 | ЭГРЭС-1 - ЦГПП - ВЛ5050 | q | line | 225129 | 63.28 | 3.164 | 129
1000622 | ЭГРЭС-1 - Нура - ВЛ5120 | q | line | 325325 | -33.07 | 0.04 | 325
1000623 | ЭГРЭС-1 - ТАВРИЧЕСКАЯ - ВЛ5577 | q | line | 4251817 | -164.71 | 0.04 | 1817
1000624 | ЭК-1150 - ЭГРЭС-1 - ВЛ5117 | q | line | 52625 | -4.78 | 0.04 | 25
1000625 | ЭК-1150 - ЭГРЭС-1 - ВЛ5107 | q | line | 62625 | -5.06 | 0.04 | 25
1000626 | ЭК-1150 - Кокшетау - ВЛ1101 | q | line | 726175 | 140.01 | 7.0005 | 175
1000627 | ЭК-1150 - Агадырь - ВЛ5170 | q | line | 826469 | 42 | 2.1 | 469
1000628 | ЭК-1150 - Алтай - ВЛ1104 | q | line | 9261660 | -435.38 | 0.04 | 1660
1000629 | ЭГРЕС-2 500 - ЭК-1150 - ВЛ5827 | q | line | 102826 | 31.64 | 1.582 | 26
1000630 | ЭГРЕС-2 500 - ЭК-1150 - ВЛ5817 | q | line | 112826 | -27.69 | 0.04 | 26
1000632 | ЕЭК - Рубцовск - ВЛ5527 | q | line | 13311621 | 115.32 | 5.766 | 1621
1000633 | ЕЭК - ИРТЫШСКАЯ - ВЛ5537 | q | line | 14311850 | -73.17 | 0.04 | 1850
1000639 | ЦГПП - ПС-ЕГПП - ВЛ5071 | q | line | 20129180 | -56.16 | 0.04 | 180
1000642 | АВРОРА 500 - ТАВРИЧЕСКАЯ - ВЛ5561 | q | line | 231471817 | 149.71 | 7.4855 | 1817
1000645 | Кокшетау - Костанай - ВЛ1102 | q | line | 26175590 | -11.87 | 0.04 | 590
1000646 | ПС-ЕГПП - Сокол - ВЛ5086 | q | line | 27180576 | -94.92 | 0.04 | 576
1000648 | Таш.ГРЭС - Шымкент - ВЛ5019 | q | line | 29224830 | -29.38 | 0.04 | 830
1000654 | Нура - Агадырь - ВЛ5138 | q | line | 35325469 | -109.43 | 0.04 | 469
1000663 | Жезказган 220 - Кумколь 220 - ЭКВ_2318_2328 | q | line | 44466467 | -29.45 | 0.04 | 467
1000668 | Агадырь - ЖЕЗКАЗГАН - ВЛ5148 | q | line | 49469480 | -6.72 | 0.04 | 480
1000669 | Агадырь - ЮКГРЭС - ВЛ5300 | q | line | 50469900 | -103.24 | 0.04 | 900
1000670 | Агадырь - ЮКГРЭС - ВЛ5320 | q | line | 51469900 | -105.02 | 0.04 | 900
1000673 | Мойынты - Агадырь 220 - ВЛ2438 | q | line | 54475468 | -23.84 | 0.04 | 468
1000676 | Костанай - Сокол - ВЛ5096 | q | line | 57590576 | 78.31 | 3.9155 | 576
1000678 | Жамбыл - Шымкент - ВЛ5169 | q | line | 59800830 | -144.48 | 0.04 | 830
1000679 | Жамбыл 220 - жгрэс-220 - ЭКВ_Жамбыл_ЖГРЭС | q | line | 60801805 | 20.65 | 1.0325 | 805
1000681 | Аспара - жгрэс-220 - ВЛ2249 | q | line | 62814805 | -27.71 | 0.04 | 805
1000682 | Шымкент 220 - Шымкентская - ВЛ2349 | q | line | 63831843 | -114.23 | 0.04 | 843
1000689 | Кентау - Ру-6 - ВЛ2519 | q | line | 70840869 | -5.22 | 0.04 | 869
1000691 | Миргалимсай - Кентау - ВЛ2549 | q | line | 72842840 | 14.2 | 0.71 | 840
1000692 | Миргалимсай - Шымкентская - ВЛ2319 | q | line | 73842843 | -28.61 | 0.04 | 843
1000695 | Жанакорган - Миргалимсай - ВЛ2539 | q | line | 76865842 | -16.35 | 0.04 | 842
1000696 | Жанакорган - Ру-6 - ВЛ2529 | q | line | 77865869 | -2.57 | 0.04 | 869
1000698 | ЮКГРЭС - Алматы - ВЛ5313 | q | line | 79900902 | -107.66 | 0.04 | 902
1000699 | ЮКГРЭС - Алма - ВЛ5363 | q | line | 80900938 | -118.63 | 0.04 | 938
1000700 | ЮКГРЭС - ЧУ - ВЛ5333 | q | line | 819009932 | -114.92 | 0.04 | 9932
1000704 | Алматы - ЧУ - ВЛ5343 | q | line | 859029932 | -170.69 | 0.04 | 9932
1000705 | Алматы 220 - АТЭЦ-3 - ВЛ2013 | q | line | 86903904 | -43.82 | 0.04 | 904
1000706 | Алматы 220 - Робот - ВЛ2053 | q | line | 87903907 | -18.2 | 0.04 | 907
1000709 | АТЭЦ-3 - Алма 220 - ВЛ2113 и ВЛ2103 | q | line | 90904939 | 35.86 | 1.793 | 939
1000712 | Западная 220 - ПС-7 АХБК - ВЛ2173 | q | line | 93918912 | 5.03 | 0.2515 | 912
1000714 | Медео - АТЭЦ-3 - ВЛ2023 | q | line | 95928904 | -35.82 | 0.04 | 904
1000716 | Шу 220 - Главная 220 - ВЛ2163 | q | line | 979321916 | -48.67 | 0.04 | 1916
1000718 | Мойнакская ГЭС - Робот | q | line | 99935907 | -22.2 | 0.04 | 907
1000720 | Алма 220 - Робот - ВЛ2463 | q | line | 101939907 | 47.8 | 2.39 | 907
1000723 | Коян-Кос - АТЭЦ-3 - ЭКВ | q | line | 104953904 | 52.36 | 2.618 | 904
1000724 | Семей - ЭК-1150 - ВЛ5370 | q | line | 10598026 | -209.27 | 0.04 | 26
1000725 | Семей - Усть-Каменогорск - ВЛ5384 | q | line | 106980240 | -140.47 | 0.04 | 240
1000726 | Семей - Актогай - ВЛ5394 | q | line | 107980986 | -77.02 | 0.04 | 986
1000729 | Актогай - Талдыкорган - ВЛ5400 | q | line | 110986987 | -95.63 | 0.04 | 987
1000730 | Талдыкорган - Алма - ВЛ5413 | q | line | 111987938 | 16.71 | 0.8355 | 938
1000732 | Рубцовск - Усть-Каменогорск - ВЛ5544 | q | line | 1131621240 | -204.73 | 0.04 | 240
1000733 | Барнаул - Рубцовск - ВЛ551 | q | line | 11416301621 | 146 | 7.3 | 1621
1000735 | Алтай - Барнаул - ВЛ596 | q | line | 11616601630 | -107.26 | 0.04 | 1630
1000736 | Алтай - Барнаул - ВЛ595 | q | line | 11716601630 | 68.27 | 3.4135 | 1630
1000739 | ТАВРИЧЕСКАЯ - ИРТЫШСКАЯ - ВЛ555 | q | line | 12018171850 | 74.02 | 3.701 | 1850
1000743 | Главная 220 - Алматы 220 - ВЛ2193 | q | line | 1241916903 | 23.32 | 1.166 | 903
1000748 | Фрунзе - Жамбыл - ВЛ5159 | q | line | 1292919800 | -134.6 | 0.04 | 800
1000750 | ТашкентТэс 220 - Шымкентская - ВЛ2419 | q | line | 1312925843 | 25.9 | 1.295 | 843
1000759 | Л-5736 (Ириклинская ГРЭС -Житикара) | q | line | 1404790577 | -75.15 | 0.04 | 577
1000761 | Л-5716 (Троицкая ГРЭС - Сокол) | q | line | 1424799576 | -67.24 | 0.04 | 576
1000762 | пр/уз жгрэс- Фрунзе - жгрэс-220 - ЭКВ | q | line | 1437223805 | -6.11 | 0.04 | 805
1000764 | пр/уз Кентау Жамбыл 220 - Жамбыл 220 - ЭКВ | q | line | 1457224801 | -40.72 | 0.04 | 801

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
25
26
27
28
29
30
31
32
33
36
37
38
39
44
50
51
52
53
54
55
56
58
59
60
61
62
101
102
103
104
108
123
124
125
126
129
130
132
134
135
136
142
143
144
147
148
150
151
153
155
156
157
159
160
161
162
163
164
165
166
167
169
170
172
173
175
176
178
179
180
186
191
214
215
218
220
221
222
240
241
242
251
306
307
308
309
310
314
315
318
325
355
383
384
450
451
452
453
454
455
457
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
480
481
482
483
484
571
572
573
574
575
576
577
578
582
585
590
592
593
594
595
596
800
801
802
803
804
805
806
807
809
810
813
814
815
816
817
830
831
834
835
836
837
838
839
840
841
842
843
844
845
846
860
861
862
863
865
866
867
869
900
901
902
903
904
907
908
909
910
911
912
913
918
924
925
928
929
930
931
932
935
937
938
939
940
941
942
950
951
953
980
981
986
987
988
1621
1622
1630
1631
1632
1636
1638
1640
1660
1671
1673
1816
1817
1850
1851
1852
1853
1854
2915
2916
2917
2918
2919
2920
2921
2922
2923
2924
2925
2926
2932
2940
2945
2950
2951
2952
3004
3005
3006
3019
3020
3102
3103
3104
4004
4701
4702
4703
4705
4709
4712
4714
4715
4727
4728
4730
4781
4782
4785
4790
4791
4798
4799
5957
5958
9001
9917
9932
47161
50001
50002
50014
50032

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
400001
400002
400003
400004
400005
400006
400007
400008
400009
400010
400011
400012
400013
400014
400015
400016
400017
400018
400019
400020
400021
400022
400023
400024
400025
400026
400027
400028
400029
400030
400031
400032
400033
400034
400035
400036
400037
400038
400039
400040
400041
400042
400043
400044
400045
400046
400047
400048
400049
400050
400051
400052
400053
400054
400055
400056
400057
400058
400059
400060
400061
400062
400063
400064
400065
400066
400067
400068
400069
400070
400071
400072
400073
400074
400075
400076
400077
400078
400079
400080
400081
400082
400083
400084
400085
400086
400087
400088
400089
400090
400091
400092
400093
400094
400095
400096
400097
400098
400099
400100
400101
400102
400103
400104
400105
400106
400107
400108
400109
400110
400111
400112
400113
400114
400115
400116
400117
400118
400119
400120
400121
400122
400123
400124
400125
400126
400127
400128
400129
400130
400131
400132
400133
400134
400135
400136
400137
400138
400139
400140
400141
400142
400143
400144
400145
400146
400147
400148
400149
400150
400151
400152
400153
400154
400155
400156
400157
400158
400159
400160
400161
400162
400163
400164
400165
400166
400167
400168
400169
400170
400171
400172
400173
400174
400175
400176
400177
400178
400179
400180
400181
400182
400183
400184
400185
400186
400187
400188
400189
400190
400191
400192
400193
400194
400195
400196
400197
400198
400199
400200
400201
400202
400203
400204
400205
400206
400207
400208
400209
400210
400211
400212
400213
400214
400215
400216
400217
400218
400219
400220
400221
400222
400223
400224
400225
400226
400227
400228
400229
400230
400231
400232
400233
400234
400235
400236
400237
400238
400239
400240
400241
400242
400243
400244
400245
400246
400247
400248
400249
400250
400251
400252
400253
400254
400255
400256
400257
400258
400259
400260
400261
400262
400263
400264
400265
400266
400267
400268
400269
400270
400271
400272
400273
400274
400275
400276
400277
400278
400279
400280
400281
400282
400283
400284
400285
400286
400287
400288
400289
400290
400291
400292
400293
400294
400295
400296
400297
400298
400299
400300
400301
400302
400303
400304
400305
400306
400307
400308
400309
400310
400311
400312
400313
400314
400315
400316
400317
400318
400319
400320
400321
400322
400323
400324
400325
400326
400327
400328
400329
400330
400331
400332
400333
400334
400335
400336
400337
400338
400339
400340
400341
400342
400343
400344
400345
400346
400347
400348
400349
400350
400351
400352
400353
400354
400355
400356
400357
400358
400359
400360
400361
400362
400363
400364
400365
400366
400367
400368
400369
400370
400371
400372
400373
400374
400375
400376
400377
400378
400379
400380
400381
400382
400383
400384

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
500001
500002
500003
500004
500005
500006
500007
500008
500009
500010
500011
500012
500013
500014
500015
500016
500017
500018
500019
500020
500021
500022
500023
500024
500025
500026
500027
500028
500029
500030
500031
500032
500033
500034
500035
500036
500037
500038
500039
500040
500041
500042
500043
500044
500045
500046
500047
500048
500049
500050
500051
500052
500053
500054
500055
500056
500057
500058
500059
500060
500061
500062
500063
500064
500065
500066
500067
500068
500069
500070
500071
500072
500073
500074

## res_ext_grid
| p_mw | q_mvar
47090

## res_load
| p_mw | q_mvar
200001
200002
200003
200004
200005
200006
200007
200008
200009
200010
200011
200012
200013
200014
200015
200016
200017
200018
200019
200020
200021
200022
200023
200024
200025
200026
200027
200028
200029
200030
200031
200032
200033
200034
200035
200036
200037
200038
200039
200040
200041
200042
200043
200044
200045
200046
200047
200048
200049
200050
200051
200052
200053
200054
200055
200056
200057
200058
200059
200060
200061
200062
200063
200064
200065
200066
200067
200068
200069
200070
200071
200072
200073
200074
200075
200076
200077
200078
200079
200080
200081
200082
200083
200084
200085
200086
200087
200088
200089
200090
200091
200092
200093
200094
200095
200096
200097
200098
200099
200100
200101
200102
200103
200104
200105
200106
200107
200108
200109
200110
200111
200112
200113
200114
200115
200116
200117
200118
200119
200120
200121
200122
200123
200124
200125
200126
200127
200128
200129
200130
200131
200132
200133
200134
200135
200136
200137
200138
200139
200140
200141
200142
200143
200144
200145
200146
200147
200148
200149
200150
200151
200152
200153
200154
200155
200156
200157
200158
200159
200160
200161
200162
200163
200164
200165
200166
200167
200168
200169
200170
200171
200172
200173
200174
200175
200176
200177
200178
200179
200180
200181
200182
200183
200184
200185
200186
200187
200188
200189
200190
200191
200192
200193
200194
200195
200196
200197
200198
200199
200200
200201
200202
200203
200204
200205
200206
200207
200208
200209
200230

## res_shunt
| p_mw | q_mvar | vm_pu
600001
600002
600003
600004
600005
600006
600007
600008
600009
600010
600011
600012
600013
600014
600015
600016
600017
600018
600019
600020
600021
600022
600023
600024
600025
600026
600027
600028
600029
600030
600031
600032
600033
600034
600035
600036
600037
600038
600039
600040
600041
600042
600043
600044
600045
600046
600047
600048
600049
600050
600051
600052
600053
600054
600055

## res_gen
| p_mw | q_mvar | va_degree | vm_pu
300001
300002
300003
300004
300005
300006
300007
300008
300009
300010
300013
300014
300015
300016
300017
300018
300019
300020
300021
300022
300023
300024
300025
300026
300027
300028
300029
300030
300031
300032
300033
300034
300035
300036
300037
300038
300039
300040
300041
300042
300043
300044
300045
300046
300047
300048
300049
300050
300051
300052
300053
300054
300055
300056
300057
300058
300059
300060
300061
300062
300063
300064
300065
300066
300067
300068
300069
300070
300071
300072
300073
300074
300075
300076
300077
300078
300079
300080
300081
300082
300083
300084
300085
300086
300087
300088
300089
300090
300091
300092
300093
300094
300095
300096
300097
300098
300099
300100
300101
300102
300103
300104
300105
300106
300107
300108
300109
300110
300111
300112
300113
300114
300115
300116
300117
300118
300119
300120
300121
300122
300123
300124
300125
300126
300127
300128
300129
300130
300131
300132
300133
300134
300135
300136
300137
300138
300139
300140
300141
300142
300143
300144
300145
300146
300147
300148
300149
300150
300151
300152
300153
300154
300155
300156
300157
300158
300159
300160
300161
300162
300163
300164
300165
300166
300167
300168
300169
300170
300171
300172
300173
300174
300175
300176
300177
300178
300179
300180
300181
300182
300183
300184
300185
300186
300187
300188
300189
300190
300191
300192
300193
300194
300195
300196
300197
300198
300199
300200
300201
300202
300203
300204
300205
300206
300207
300208
300209

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | gen | name | object
16 | gen | bus | uint32
17 | gen | p_mw | float64
18 | gen | vm_pu | float64
19 | gen | sn_mva | float64
20 | gen | min_q_mvar | float64
21 | gen | max_q_mvar | float64
22 | gen | scaling | float64
23 | gen | slack | bool
24 | gen | in_service | bool
25 | gen | slack_weight | float64
26 | gen | type | object
27 | gen | power_station_trafo | float64
28 | shunt | bus | uint32
29 | shunt | name | object
30 | shunt | q_mvar | float64
31 | shunt | p_mw | float64
32 | shunt | vn_kv | float64
33 | shunt | step | uint32
34 | shunt | max_step | uint32
35 | shunt | in_service | bool
36 | ext_grid | name | object
37 | ext_grid | bus | uint32
38 | ext_grid | vm_pu | float64
39 | ext_grid | va_degree | float64
40 | ext_grid | slack_weight | float64
41 | ext_grid | in_service | bool
42 | line | name | object
43 | line | std_type | object
44 | line | from_bus | uint32
45 | line | to_bus | uint32
46 | line | length_km | float64
47 | line | r_ohm_per_km | float64
48 | line | x_ohm_per_km | float64
49 | line | c_nf_per_km | float64
50 | line | g_us_per_km | float64
51 | line | max_i_ka | float64
52 | line | df | float64
53 | line | parallel | uint32
54 | line | type | object
55 | line | in_service | bool
56 | trafo | name | object
57 | trafo | std_type | object
58 | trafo | hv_bus | uint32
59 | trafo | lv_bus | uint32
60 | trafo | sn_mva | float64
61 | trafo | vn_hv_kv | float64
62 | trafo | vn_lv_kv | float64
63 | trafo | vk_percent | float64
64 | trafo | vkr_percent | float64
65 | trafo | pfe_kw | float64
66 | trafo | i0_percent | float64
67 | trafo | shift_degree | float64
68 | trafo | tap_side | object
69 | trafo | tap_neutral | float64
70 | trafo | tap_min | float64
71 | trafo | tap_max | float64
72 | trafo | tap_step_percent | float64
73 | trafo | tap_step_degree | float64
74 | trafo | tap_pos | float64
75 | trafo | tap_phase_shifter | bool
76 | trafo | parallel | uint32
77 | trafo | df | float64
78 | trafo | in_service | bool
79 | trafo | pt_percent | float64
80 | trafo | oltc | object
81 | trafo | Unnamed: 26 | float64
82 | trafo | Unnamed: 27 | int64
83 | trafo | Unnamed: 28 | int64
84 | measurement | name | object
85 | measurement | measurement_type | object
86 | measurement | element_type | object
87 | measurement | element | int64
88 | measurement | value | float64
89 | measurement | std_dev | float64
90 | measurement | side | float64
91 | res_bus | vm_pu | float64
92 | res_bus | va_degree | float64
93 | res_bus | p_mw | float64
94 | res_bus | q_mvar | float64
95 | res_line | p_from_mw | float64
96 | res_line | q_from_mvar | float64
97 | res_line | p_to_mw | float64
98 | res_line | q_to_mvar | float64
99 | res_line | pl_mw | float64
100 | res_line | ql_mvar | float64
101 | res_line | i_from_ka | float64
102 | res_line | i_to_ka | float64
103 | res_line | i_ka | float64
104 | res_line | vm_from_pu | float64
105 | res_line | va_from_degree | float64
106 | res_line | vm_to_pu | float64
107 | res_line | va_to_degree | float64
108 | res_line | loading_percent | float64
109 | res_trafo | p_hv_mw | float64
110 | res_trafo | q_hv_mvar | float64
111 | res_trafo | p_lv_mw | float64
112 | res_trafo | q_lv_mvar | float64
113 | res_trafo | pl_mw | float64
114 | res_trafo | ql_mvar | float64
115 | res_trafo | i_hv_ka | float64
116 | res_trafo | i_lv_ka | float64
117 | res_trafo | vm_hv_pu | float64
118 | res_trafo | va_hv_degree | float64
119 | res_trafo | vm_lv_pu | float64
120 | res_trafo | va_lv_degree | float64
121 | res_trafo | loading_percent | float64
122 | res_ext_grid | p_mw | float64
123 | res_ext_grid | q_mvar | float64
124 | res_load | p_mw | float64
125 | res_load | q_mvar | float64
126 | res_shunt | p_mw | float64
127 | res_shunt | q_mvar | float64
128 | res_shunt | vm_pu | float64
129 | res_gen | p_mw | float64
130 | res_gen | q_mvar | float64
131 | res_gen | va_degree | float64
132 | res_gen | vm_pu | float64