## parameters
| version | converged | name | f_hz | sn_mva
0 | 2.9.0 | FALSE |  | 50 | 1

## bus
| name | vn_kv | type | zone | in_service
1 | ЭК-1150 | 500 | b | сз | TRUE
2 | ЭГРЭС-1 | 500 | b | сз | TRUE
3 | Нура | 500 | b | сз | TRUE
4 | Агадырь | 500 | b | сз | TRUE
5 | ЮКГРЭС | 500 | b | юз | TRUE
6 | Алматы | 500 | b | юз | TRUE
7 | Алма | 500 | b | юз | TRUE
8 | ЧУ | 500 | b | юз | TRUE
9 | Фрунзе | 500 | b | ца | TRUE
10 | Жамбыл | 500 | b | юз | TRUE
11 | Шымкент | 500 | b | юз | TRUE
12 | Семей | 500 | b | сз | TRUE
13 | Актогай | 500 | b | сз | TRUE
14 | Талдыкорган | 500 | b | юз | TRUE
15 | Усть-Каменогорск | 500 | b | сз | TRUE
16 | Ташкент | 500 | b | ца | TRUE
17 | ЦГПП | 500 | b | сз | TRUE
18 | ЕЭК | 500 | b | сз | TRUE
19 | Рубцовск | 500 | b | рф | TRUE
20 | Алтай | 500 | b | рф | TRUE
21 | Агадырь220 | 220 | b | сз | TRUE

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
1 | БАЗА (ЭК-1150) | 1 | 1.024 | 0 | 1 | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
2 | ЭГРЭС-1 | 2 | 470 | -100 | 0 | 0 |  | 1 | TRUE | wye
3 | Нура | 3 | 1250 | 180 | 0 | 0 |  | 1 | TRUE | wye
4 | Агадырь220 | 21 | 300 | -200 | 0 | 0 |  | 1 | TRUE | wye
5 | ЮКГРЭС | 5 | 62 | 0.5 | 0 | 0 |  | 1 | TRUE | wye
6 | Алматы | 6 | 820 | 100 | 0 | 0 |  | 1 | TRUE | wye
7 | Алма | 7 | 820 | 6 | 0 | 0 |  | 1 | TRUE | wye
8 | ЧУ | 8 | 180 | 11 | 0 | 0 |  | 1 | TRUE | wye
9 | Фрунзе | 9 | 520 | 50 | 0 | 0 |  | 1 | TRUE | wye
10 | Жамбыл | 10 | 410 | 40 | 0 | 0 |  | 1 | TRUE | wye
11 | Шымкент | 11 | 420 | 63.4 | 0 | 0 |  | 1 | TRUE | wye
12 | Семей | 12 | 160 | -20 | 0 | 0 |  | 1 | TRUE | wye
14 | Талдыкорган | 14 | 160 | 9 | 0 | 0 |  | 1 | TRUE | wye
15 | Усть-Каменогорск | 15 | 990 | 440 | 0 | 0 |  | 1 | TRUE | wye
17 | ЦГПП | 17 | 930 | 12 | 0 | 0 |  | 1 | TRUE | wye
18 | ЕЭК | 18 | 820 | -100 | 0 | 0 |  | 1 | TRUE | wye

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service | pt_percent | oltc
1 | agadyr |  | 20 | 21 | 501 | 500 | 220 | 11 | 0.189 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE

## gen
| name | bus | p_mw | vm_pu | sn_mva | min_q_mvar | max_q_mvar | scaling | slack | in_service | slack_weight | type | power_station_trafo
2 | ЭГРЭС-1 | 2 | 2120 | 1.029 |  | -420 | 1200 | 1 | FALSE | TRUE | 0
3 | Нура | 3 | 1150 | 1.014 |  | -360 | 150 | 1 | FALSE | TRUE | 0
15 | Усть-Каменогорск | 15 | 1120 | 1.01 |  | -480 | 350 | 1 | FALSE | TRUE | 0
18 | ЕЭК | 18 | 890 | 1.018 |  | -400 | 150 | 1 | FALSE | TRUE | 0
6 | Алматы | 6 | 560 | 1.01 |  | -200 | 60 | 1 | FALSE | TRUE | 0
7 | Алма | 7 | 545 | 1.01 |  | -180 |  | 1 | FALSE | TRUE | 0
16 | Ташкент | 16 | 450 | 0.997 |  | -200 | 20 | 1 | FALSE | TRUE | 0
9 | Фрунзе | 9 | 330 | 1.02 |  | -122 | 198 | 1 | FALSE | TRUE | 0
17 | ЦГПП | 17 | 300 | 1.026 |  | -120 | 140 | 1 | FALSE | TRUE | 0
10 | Жамбыл | 10 | 240 | 1.01 |  | -200 | 150 | 1 | FALSE | TRUE | 0
12 | Семей | 12 | 150 | 1.006 |  | -300 | 90 | 1 | FALSE | TRUE | 0
20 | Алтай | 20 | 77 | 1.032 |  |  |  | 1 | FALSE | TRUE | 0
14 | Талдыкорган | 14 | 40 | 1.01 |  | -180 |  | 1 | FALSE | TRUE | 0

## shunt
| bus | name | q_mvar | p_mw | vn_kv | step | max_step | in_service
2 | 2 | ЭГРЭС-1 | 518.5674 | 0 | 514.5 | 1 | 1 | TRUE
4 | 4 | Агадырь | 343.6987 | 0 | 513 | 1 | 1 | TRUE
5 | 5 | ЮКГРЭС | 346.2995 | 0 | 514.9373 | 1 | 1 | TRUE
6 | 6 | Алматы | 166.5313 | 0 | 505 | 1 | 1 | TRUE
7 | 7 | Алма | 166.5313 | 0 | 505 | 1 | 1 | TRUE
8 | 8 | ЧУ | 170.9278 | 0 | 511.6227 | 1 | 1 | TRUE
9 | 9 | Фрунзе | 169.8453 | 0 | 510 | 1 | 1 | TRUE
10 | 10 | Жамбыл | 166.5313 | 0 | 505 | 1 | 1 | TRUE
12 | 12 | Семей | 166.6646 | 0 | 505.2021 | 1 | 1 | TRUE
17 | 17 | ЦГПП | 169.8612 | 0 | 510.0239 | 1 | 1 | TRUE
19 | 19 | Рубцовск | 326.7871 | 0 | 500.2198 | 1 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | ЭК-1150 - ЭГРЭС-1 |  | 1 | 2 | 1 | 0.31 | 3.81 | 0.15311 | 0 | 414.226 | 1 | 1 |  | TRUE
1 | ЭК-1150 - ЭГРЭС-1 |  | 1 | 2 | 1 | 0.25 | 3.15 | 0.12637 | 0 | 498.6571 | 1 | 1 |  | TRUE
2 | ЭГРЭС-1 - Нура |  | 2 | 3 | 1 | 8.3 | 78.3 | 3.3424 | 0 | 696.4586 | 1 | 1 |  | TRUE
3 | Нура - Агадырь |  | 3 | 4 | 1 | 6.86 | 79.4 | 3.1864 | 0 | 602.8181 | 1 | 1 |  | TRUE
4 | ЭК-1150 - Агадырь |  | 1 | 4 | 1 | 11.6 | 138.3 | 5.5941 | 0 | 740.0821 | 1 | 1 |  | TRUE
5 | Агадырь - ЮКГРЭС |  | 4 | 5 | 1 | 12.7 | 115.6 | 4.8576 | 0 | 520.3914 | 1 | 1 |  | TRUE
6 | Агадырь - ЮКГРЭС |  | 4 | 5 | 1 | 11.5 | 118.41 | 4.6067 | 0 | 503.2357 | 1 | 1 |  | TRUE
7 | ЮКГРЭС - Алматы |  | 5 | 6 | 1 | 9.35 | 85 | 3.5811 | 0 | 299.5161 | 1 | 1 |  | TRUE
8 | ЮКГРЭС - Алма |  | 5 | 7 | 1 | 9.2 | 98.2 | 3.6543 | 0 | 257.0298 | 1 | 1 |  | TRUE
9 | ЮКГРЭС - ЧУ |  | 5 | 8 | 1 | 5.2 | 63.6 | 2.5084 | 0 | 461.5078 | 1 | 1 |  | TRUE
10 | Алматы - ЧУ |  | 6 | 8 | 1 | 7.1 | 72.41 | 2.8999 | 0 | 237.1968 | 1 | 1 |  | TRUE
11 | Алматы - Алма |  | 6 | 7 | 1 | 1.8 | 19.5 | 0.72258 | 0 | 213.9712 | 1 | 1 |  | TRUE
12 | ЧУ - Фрунзе |  | 8 | 9 | 1 | 2.82 | 28.85 | 1.1523 | 0 | 380.6326 | 1 | 1 |  | TRUE
13 | Фрунзе - Жамбыл |  | 9 | 10 | 1 | 6 | 69 | 2.5816 | 0 | 216.7461 | 1 | 1 |  | TRUE
14 | Жамбыл - Шымкент |  | 10 | 11 | 1 | 4.1 | 51.6 | 1.9481 | 0 | 117.9305 | 1 | 1 |  | TRUE
15 | Семей - ЭК-1150 |  | 12 | 1 | 1 | 10.1 | 122.52 | 4.8505 | 0 | 348.8965 | 1 | 1 |  | TRUE
16 | Семей - Актогай |  | 12 | 13 | 1 | 9.77 | 119.59 | 4.5036 | 0 | 573.7618 | 1 | 1 |  | TRUE
17 | Актогай - Талдыкорган |  | 13 | 14 | 1 | 8.33 | 88.52 | 3.2936 | 0 | 526.8543 | 1 | 1 |  | TRUE
18 | Талдыкорган - Алма |  | 14 | 7 | 1 | 5.91 | 62.76 | 2.3352 | 0 | 390.6799 | 1 | 1 |  | TRUE
19 | Семей - Усть-Каменогорск |  | 12 | 15 | 1 | 5.72 | 58.55 | 2.2944 | 0 | 295.1596 | 1 | 1 |  | TRUE
20 | Ташкент - Шымкент |  | 16 | 11 | 1 | 3 | 32.5 | 1.4484 | 0 | 550.641 | 1 | 1 |  | TRUE
21 | ЭГРЭС-1 - ЦГПП |  | 2 | 17 | 1 | 7.3 | 89.75 | 3.3796 | 0 | 727.8692 | 1 | 1 |  | TRUE
22 | ЭГРЭС-1 - ЕЭК |  | 2 | 18 | 1 | 3.05 | 36.64 | 1.4732 | 0 | 156.277 | 1 | 1 |  | TRUE
23 | ЕЭК - Рубцовск |  | 18 | 19 | 1 | 10.25 | 98.5 | 4.1063 | 0 | 253.1502 | 1 | 1 |  | TRUE
24 | Рубцовск - Усть-Каменогорск |  | 19 | 15 | 1 | 4.34 | 44.02 | 1.7826 | 0 | 195.2117 | 1 | 1 |  | TRUE
25 | ЭК-1150 - Алтай |  | 1 | 20 | 1 | 14.79 | 212.33 | 9.123 | 0 | 439.5948 | 1 | 1 |  | TRUE

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## res_bus_est
| vm_pu | va_degree | p_mw | q_mvar
1
2
3

## res_line_est
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0
1
2

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | sgen | name | object
6 | sgen | bus | int64
7 | sgen | p_mw | float64
8 | sgen | q_mvar | float64
9 | sgen | sn_mva | float64
10 | sgen | scaling | float64
11 | sgen | in_service | bool
12 | sgen | type | object
13 | sgen | current_source | bool
14 | sgen | min_p_mw | float64
15 | sgen | max_p_mw | float64
16 | sgen | min_q_mvar | float64
17 | sgen | max_q_mvar | float64
18 | sgen | k | float64
19 | sgen | rx | float64
20 | sgen | controllable | object
21 | ext_grid | name | object
22 | ext_grid | bus | uint32
23 | ext_grid | vm_pu | float64
24 | ext_grid | va_degree | float64
25 | ext_grid | slack_weight | float64
26 | ext_grid | in_service | bool
27 | line | name | object
28 | line | std_type | object
29 | line | from_bus | uint32
30 | line | to_bus | uint32
31 | line | length_km | float64
32 | line | r_ohm_per_km | float64
33 | line | x_ohm_per_km | float64
34 | line | c_nf_per_km | float64
35 | line | g_us_per_km | float64
36 | line | max_i_ka | float64
37 | line | df | float64
38 | line | parallel | uint32
39 | line | type | object
40 | line | in_service | bool
41 | measurement | name | object
42 | measurement | measurement_type | object
43 | measurement | element_type | object
44 | measurement | element | uint32
45 | measurement | value | float64
46 | measurement | std_dev | float64
47 | measurement | side | object
48 | res_bus_est | vm_pu | float64
49 | res_bus_est | va_degree | float64
50 | res_bus_est | p_mw | float64
51 | res_bus_est | q_mvar | float64
52 | res_line_est | p_from_mw | float64
53 | res_line_est | q_from_mvar | float64
54 | res_line_est | p_to_mw | float64
55 | res_line_est | q_to_mvar | float64
56 | res_line_est | pl_mw | float64
57 | res_line_est | ql_mvar | float64
58 | res_line_est | i_from_ka | float64
59 | res_line_est | i_to_ka | float64
60 | res_line_est | i_ka | float64
61 | res_line_est | vm_from_pu | float64
62 | res_line_est | va_from_degree | float64
63 | res_line_est | vm_to_pu | float64
64 | res_line_est | va_to_degree | float64
65 | res_line_est | loading_percent | float64