## parameters
| version | converged | name | OPF_converged
0 | 2.9.0 | FALSE |  | FALSE

## bus
| name | vn_kv | type | zone | in_service
25 | ЭГРЭС-1-500 | 500 | b | 2 | TRUE
26 | ЭКИБАСТУЗСКАЯ | 500 | b | 2 | TRUE
27 | КЭЗ-1.2 | 500 | b | 2 | TRUE
28 | ЭГРЭС-2-500 | 500 | b | 2 | TRUE
29 | эгрэс-2-220 | 220 | b | 2 | TRUE
30 | еэк-20-бл5-8 | 20 | b | 2 | TRUE
31 | ЕЭК-500 | 500 | b | 2 | TRUE
32 | еэк-20-бл2-4 | 20 | b | 2 | TRUE
33 | еэк-220 | 220 | b | 2 | TRUE
36 | Калкаман | 220 | b | 2 | TRUE
37 | нс-7 | 220 | b | 2 | FALSE
38 | Экибастуз-220 | 220 | b | 2 | TRUE
39 | эгрэс-1 | 220 | b | 2 | TRUE
44 | Экибастузская тэц | 6.2 | b | 2 | FALSE
50 | эгрэс-1-бл2 | 20 | b | 2 | TRUE
51 | эгрэс-1-бл3-8 | 19.8 | b | 2 | TRUE
52 | нс-12 | 220 | b | 2 | FALSE
53 | ээпк | 220 | b | 2 | TRUE
54 | црмз | 220 | b | 2 | TRUE
55 | азф | 220 | b | 2 | FALSE
56 | Строительная-2 | 220 | b | 2 | TRUE
58 | Уленты (т) | 220 | b | 2 | TRUE
59 | Бощак(T) | 220 | b | 2 | TRUE
60 | эгрэс-2-20 | 19.6 | b | 2 | TRUE
61 | Таскудык(Т) | 220 | b | 2 | TRUE
62 | бгок | 220 | b | 2 | TRUE
101 | Шоптыколь (т) | 220 | b | 5 | TRUE
102 | Батыс | 220 | b | 90 | TRUE
103 | Достык | 220 | b | 90 | TRUE
104 | Шыгыс | 220 | b | 90 | TRUE
108 | Акмолинская ТЭЦ | 220 | b | 90 | TRUE
123 | Жолымбет | 220 | b | 5 | TRUE
124 | цгпп | 110 | b | 5 | TRUE
125 | Шортанды (т) | 220 | b | 5 | FALSE
126 | Бурабай (т) | 220 | b | 6 | TRUE
129 | ЦГПП | 500 | b | 5 | TRUE
130 | цгпп | 220 | b | 5 | TRUE
132 | Жалтыр (т) | 220 | b | 5 | TRUE
134 | Атбасар | 220 | b | 5 | TRUE
135 | кгпп | 220 | b | 6 | TRUE
136 | Киялы | 220 | b | 7 | TRUE
142 | птэц-2-110 | 110 | b | 7 | TRUE
143 | Смирново | 220 | b | 7 | TRUE
144 | птэц-2-220 | 220 | b | 7 | TRUE
147 | АВРОРА | 500 | b | 7 | TRUE
148 | Аврора | 220 | b | 7 | TRUE
150 | Макинск | 220 | b | 5 | TRUE
151 | Степная | 220 | b | 6 | TRUE
153 | Янко (т) | 220 | b | 6 | TRUE
155 | вэс ерейментау | 220 | b | 5 | TRUE
156 | Уголки(т) | 220 | b | 6 | TRUE
157 | Куйбышевская | 220 | b | 6 | TRUE
159 | Красноармейская | 220 | b | 7 | TRUE
160 | Сибирь | 110 | b | 7 | FALSE
161 | Сибирь | 220 | b | 7 | FALSE
162 | Тастак (т) | 220 | b | 5 | FALSE
163 | Ирченко (т) | 220 | b | 5 | FALSE
164 | Жаксы (т) | 220 | b | 5 | FALSE
165 | оп-80 (т) | 220 | b | 5 | FALSE
166 | Ерментау (т) | 220 | b | 5 | TRUE
167 | Еркеншилик (т) | 220 | b | 5 | TRUE
169 | Сары-оба (т) | 220 | b | 5 | FALSE
170 | Есиль | 220 | b | 5 | TRUE
172 | Перекатная (т) | 220 | b | 5 | TRUE
173 | Буран | 220 | b | 6 | TRUE
175 | КОКЧЕТАВСКАЯ | 500 | b | 6 | TRUE
176 | Кокшетауская-1150 | 220 | b | 6 | TRUE
178 | Ельтай (т) | 220 | b | 5 | FALSE
179 | Танкерис (т) | 220 | b | 5 | TRUE
180 | ЕСИЛЬ | 500 | b | 5 | TRUE
186 | Чернозубовка | 220 | b | 6 | TRUE
191 | wtu 2.0 | 35 | b | 5 | FALSE
214 | пс-14 | 220 | b | 1 | TRUE
215 | ПС-7 | 220 | b | 1 | TRUE
218 | пс-18 | 220 | b | 19 | TRUE
220 | шгэс-220 | 220 | b | 19 | TRUE
221 | шгэс-14 | 13.8 | b | 19 | TRUE
222 | жгок | 220 | b | 19 | TRUE
240 | УСТЬ-КАМЕНОГРСКАЯ-500 | 500 | b | 1 | TRUE
241 | Усть-Камногорская-220 | 220 | b | 1 | TRUE
242 | ТМК | 220 | b | 1 | TRUE
251 | пс 51 | 220 | b | 19 | TRUE
306 | Осакаровка | 220 | b | 3 | TRUE
307 | нс 17 | 220 | b | 3 | FALSE
308 | Cарань | 220 | b | 3 | TRUE
309 | нс-19 | 220 | b | 3 | TRUE
310 | Нура-220 | 220 | b | 3 | TRUE
314 | отпайка-4 | 220 | b | 3 | TRUE
315 | отпайка-5 | 220 | b | 3 | TRUE
318 | ипм | 220 | b | 3 | FALSE
325 | НУРА-500 | 500 | b | 3 | TRUE
355 | грэс-2 | 220 | b | 4 | TRUE
383 | тэц-3 | 220 | b | 3 | TRUE
384 | Металлургическая | 220 | b | 3 | TRUE
450 | Кара-мурун | 220 | b | 4 | FALSE
451 | Жарык | 220 | b | 4 | FALSE
452 | Айса | 220 | b | 4 | TRUE
453 | Жана-арка | 220 | b | 4 | TRUE
454 | Барсенгир | 220 | b | 4 | TRUE
455 | Кумколь | 110 | b | 4 | TRUE
457 | Кайракты | 220 | b | 4 | TRUE
461 | Никольская | 110 | b | 4 | FALSE
462 | жтэц | 110 | b | 4 | FALSE
463 | жтэц-220 | 220 | b | 4 | TRUE
464 | Никольская | 220 | b | 4 | TRUE
465 | Kаражал | 220 | b | 4 | TRUE
466 | Жезказган-220 | 220 | b | 4 | TRUE
467 | Кумколь | 220 | b | 4 | TRUE
468 | Aгадырь-220 | 220 | b | 4 | TRUE
469 | АГАДЫРЬ-500 | 500 | b | 4 | TRUE
470 | бтэц-10 | 10 | b | 4 | FALSE
471 | бтэц-110 | 110 | b | 4 | TRUE
472 | Балхашская-110 | 110 | b | 4 | TRUE
473 | Балхашская-220 | 220 | b | 4 | TRUE
474 | Акчтау | 220 | b | 4 | TRUE
475 | Mоинты | 220 | b | 4 | TRUE
476 | Каражингил | 220 | b | 4 | FALSE
477 | Сарышаган | 220 | b | 4 | FALSE
480 | ЖЕЗКАЗГАН-500 | 500 | b | 4 | TRUE
481 | Коунрад-220 | 220 | b | 4 | TRUE
482 | Коунрад-110 | 110 | b | 4 | FALSE
483 | Актогай-220 | 220 | b | 4 | TRUE
484 | Актогай-110 | 110 | b | 4 | TRUE
571 | Кушмурун | 220 | b | 8 | FALSE
572 | Аман-карагай | 220 | b | 8 | FALSE
573 | Апановка | 220 | b | 8 | TRUE
574 | Лисаковка | 220 | b | 8 | TRUE
575 | Сокол-220 | 220 | b | 8 | TRUE
576 | СОКОЛ-500 | 500 | b | 8 | TRUE
577 | ЖИТИКАРА-500 | 500 | b | 8 | TRUE
578 | Житикара-110 | 110 | b | 8 | TRUE
582 | Качары | 220 | b | 8 | TRUE
585 | Челгаши | 220 | b | 8 | FALSE
590 | КОСТАНАЙСКАЯ | 500 | b | 8 | TRUE
592 | Кустанайская | 220 | b | 8 | TRUE
593 | Центральная | 220 | b | 8 | TRUE
594 | ссгпо | 220 | b | 8 | TRUE
595 | Приуральская | 220 | b | 8 | TRUE
596 | Заречная | 220 | b | 8 | TRUE
800 | ЖАМБЫЛ | 500 | b | 11 | TRUE
801 | Жамбыл | 220 | b | 11 | TRUE
802 | Бурное | 220 | b | 11 | TRUE
803 | Каратау | 220 | b | 11 | TRUE
804 | Опорная | 220 | b | 11 | TRUE
805 | жгрэс-220 | 220 | b | 11 | TRUE
806 | жгрэс-16 | 16.07 | b | 11 | FALSE
807 | жгрэс-110 | 110 | b | 11 | FALSE
809 | Мерке | 220 | b | 11 | TRUE
810 | сэс бурное | 220 | b | 11 | TRUE
813 | Шымкентская ТЭЦ-3 | 220 | b | 12 | TRUE
814 | Аспара | 220 | b | 11 | TRUE
815 | Жамбыл Тяга | 220 | b | 11 | TRUE
816 | Бурное Тяга | 220 | b | 11 | FALSE
817 | Абдезим | 220 | b | 11 | FALSE
830 | ШЫМКЕНТ-500 | 500 | b | 12 | TRUE
831 | Шымкент-220 | 220 | b | 12 | TRUE
834 | Сас-тюбе | 220 | b | 12 | TRUE
835 | Ванновка | 220 | b | 12 | TRUE
836 | Бадам | 220 | b | 12 | FALSE
837 | Арысь | 220 | b | 12 | FALSE
838 | Монтайташ | 220 | b | 12 | FALSE
839 | Жылга | 220 | b | 12 | TRUE
840 | Кентау | 220 | b | 12 | TRUE
841 | Шолаккорган | 220 | b | 12 | TRUE
842 | Миргалимсай | 220 | b | 12 | TRUE
843 | Шымкентская | 220 | b | 12 | TRUE
844 | Тюлькубас | 220 | b | 12 | FALSE
845 | Кызылсай | 220 | b | 12 | TRUE
846 | гнпс | 220 | b | 12 | TRUE
860 | Кызылординская тэц | 220 | b | 13 | TRUE
861 | отпайка | 220 | b | 13 | TRUE
862 | Кызылординская | 220 | b | 13 | TRUE
863 | Шиели | 220 | b | 13 | TRUE
865 | Жанакорган | 220 | b | 13 | TRUE
866 | Жалагаш | 220 | b | 13 | FALSE
867 | Жусалы | 220 | b | 13 | FALSE
869 | Ру-6 | 220 | b | 13 | TRUE
900 | ЮКГРЭС | 500 | b | 9 | TRUE
901 | юкгрэс | 220 | b | 9 | TRUE
902 | АЛМАТЫ | 500 | b | 9 | TRUE
903 | Алматы | 220 | b | 9 | TRUE
904 | тэц-3 2сш | 220 | b | 9 | TRUE
907 | Робот | 220 | b | 9 | TRUE
908 | пс-62 АТ2 | 220 | b | 9 | TRUE
909 | Капчагайская гэс-220 | 220 | b | 9 | TRUE
910 | Капчагайская гэс-14 | 13.8 | b | 9 | FALSE
911 | Чилик | 220 | b | 9 | TRUE
912 | пс-7 | 220 | b | 9 | TRUE
913 | пс-7 | 110 | b | 9 | TRUE
918 | Западная | 220 | b | 9 | TRUE
924 | Мынарал | 220 | b | 9 | FALSE
925 | Чиганак | 220 | b | 9 | TRUE
928 | Медео | 220 | b | 9 | TRUE
929 | Таугуль | 220 | b | 9 | TRUE
930 | Кияхты | 220 | b | 9 | FALSE
931 | Жидели | 220 | b | 9 | FALSE
932 | Шу | 220 | b | 9 | TRUE
935 | Мойнакская гэс-220 | 220 | b | 9 | TRUE
937 | Мойнакская гэс-15-1 | 15.75 | b | 9 | FALSE
938 | АЛМА | 500 | b | 9 | TRUE
939 | Алма | 220 | b | 9 | TRUE
940 | Бесагаш | 220 | b | 9 | TRUE
941 | Мойнакская гэс-15-2 | 15.75 | b | 9 | FALSE
942 | Ерменсай | 220 | b | 9 | TRUE
950 | Сары-Озек | 220 | b | 10 | TRUE
951 | Талдыкорганская-220 | 220 | b | 10 | TRUE
953 | Коян-Кос | 220 | b | 9 | TRUE
980 | СЕМЕЙ-500 | 500 | b | 19 | TRUE
981 | Семей-220 | 220 | b | 19 | TRUE
986 | АКТОГАЙ | 500 | b | 4 | TRUE
987 | ТАЛДЫКОРГАН-500 | 500 | b | 10 | TRUE
988 | Талдыкорган-220 | 220 | b | 10 | TRUE
1621 | РУБЦОВСКАЯ | 500 | b | 15 | TRUE
1622 | Рубцовская | 220 | b | 15 | TRUE
1630 | БАРНАУЛ-500 | 500 | b | 15 | TRUE
1631 | ЗАРЯ | 500 | b | 15 | TRUE
1632 | Юрга | 500 | b | 0 | FALSE
1636 | Итатская | 500 | b | 0 | FALSE
1638 | Новокузнецкая | 500 | b | 0 | FALSE
1640 | Барнаул-220 | 220 | b | 15 | FALSE
1660 | АЛТАЙ | 500 | b | 15 | TRUE
1671 | Барабинская-220 | 220 | b | 0 | FALSE
1673 | Урожайная | 220 | b | 15 | FALSE
1816 | Таврическая | 220 | b | 17 | TRUE
1817 | ТАВРИЧЕСКАЯ | 500 | b | 17 | TRUE
1850 | ИРТЫШСКАЯ | 500 | b | 17 | TRUE
1851 | Иртышская | 220 | b | 17 | FALSE
1852 | ВИТЯЗЬ | 500 | b | 17 | TRUE
1853 | ВОСХОД | 500 | b | 17 | TRUE
1854 | Восход | 220 | b | 17 | TRUE
2915 | ТУЛЕБЕРДЫЕВА | 500 | b | 51 | FALSE
2916 | Главная | 220 | b | 50 | TRUE
2917 | Карабалты | 220 | b | 50 | FALSE
2918 | Бишкек | 220 | b | 50 | TRUE
2919 | ФРУНЗЕ | 500 | b | 50 | TRUE
2920 | ЛОЧИН | 500 | b | 18 | FALSE
2921 | ТОКТОГУЛЬСКАЯ ГЭС | 500 | b | 51 | TRUE
2922 | УЗБЕКИСТОН | 500 | b | 18 | FALSE
2923 | СЫРДАРЬИНСКАЯ ТЭС | 500 | b | 18 | FALSE
2924 | ТАШ.ГРЭС | 500 | b | 18 | TRUE
2925 | Ташкент | 220 | b | 18 | TRUE
2926 | Ташкентская грэс | 220 | b | 18 | FALSE
2932 | Чуйская | 220 | b | 51 | FALSE
2940 | ТАШКЕНТ | 500 | b | 18 | FALSE
2945 | НОВО-АНГРЕНСКАЯ ТЭС | 500 | b | 18 | FALSE
2950 | ДАТКА | 500 | b | 51 | FALSE
2951 | КЕМИН | 500 | b | 51 | TRUE
2952 | Кемин | 220 | b | 51 | TRUE
3004 | Акжар | 220 | b | 33 | FALSE
3005 | Кимперсай | 220 | b | 33 | FALSE
3006 | Актюбе-220 | 220 | b | 33 | FALSE
3019 | Чилисай | 220 | b | 33 | FALSE
3020 | Ульке-220 | 220 | b | 33 | FALSE
3102 | Рысаево | 220 | b | 16 | FALSE
3103 | Новотроицк | 220 | b | 16 | FALSE
3104 | Орская | 220 | b | 16 | FALSE
4004 | арбз | 110 | b | 33 | FALSE
4701 | ЮЖНАЯ | 500 | b | 16 | TRUE
4702 | РЕФТИНСКАЯ ГРЭС | 500 | b | 16 | TRUE
4703 | КОЗЫРЕВО | 500 | b | 16 | TRUE
4705 | ЧЕЛЯБИНСК | 500 | b | 16 | TRUE
4709 | БЕКЕТОВО | 500 | b | 16 | TRUE
4712 | УФИМСКАЯ | 500 | b | 16 | TRUE
4714 | КРОПАЧЕВО | 500 | b | 16 | TRUE
4715 | ЗЛАТОУСТ | 500 | b | 16 | TRUE
4727 | КУРГАН | 500 | b | 16 | TRUE
4728 | БЕРКУТ | 500 | b | 35 | TRUE
4730 | ТЮМЕНЬ | 500 | b | 35 | TRUE
4781 | Макушино | 220 | b | 16 | FALSE
4782 | ШАГОЛ | 500 | b | 16 | TRUE
4785 | МАГНИТОГОРСКАЯ | 500 | b | 16 | TRUE
4790 | ИРИКЛИНСКАЯ ГРЭС | 500 | b | 16 | TRUE
4791 | Ириклинская грэс | 220 | b | 16 | FALSE
4798 | Троицкая грэс | 220 | b | 16 | TRUE
4799 | ТРОИЦКАЯ ГРЭС | 500 | b | 16 | TRUE
5957 | гпп-2 | 220 | b | 14 | TRUE
5958 | гпп-1 | 220 | b | 14 | FALSE
9001 | УЛЬКЕ-500 | 500 | b | 33 | FALSE
9917 | БАРАБИНСКАЯ | 500 | b | 15 | TRUE
9932 | ШУ | 500 | b | 9 | TRUE
47161 | ЮЖНОУРАЛЬСКАЯ ГРЭС-2 | 500 | b | 16 | TRUE
50001 | ИСЕТЬ | 500 | b | 16 | TRUE
50002 | КУРЧАТОВСКАЯ | 500 | b | 16 | TRUE
50014 | СМЕЛОВСКАЯ | 500 | b | 16 | TRUE
50032 | ПРИВАЛОВСКАЯ | 500 | b | 16 | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
200001 | Ульке-220 | 3020 | 172 | 39 | 0 | 0 |  | 1 | FALSE | wye
200002 | Кимперсай | 3005 | 63 | 16 | 0 | 0 |  | 1 | FALSE | wye
200003 | Актюбе-220 | 3006 | 256 | 110 | 0 | 0 |  | 1 | FALSE | wye
200004 | НОВО-АНГРЕНСКАЯ ТЭС | 2945 | 75 | 293 | 0 | 0 |  | 1 | FALSE | wye
200005 | тэц-3 | 383 | 410 | 200 | 0 | 0 |  | 1 | TRUE | wye
200006 | Металлургическая | 384 | 440 | 250 | 0 | 0 |  | 1 | TRUE | wye
200007 | Чилисай | 3019 | 157 | 17 | 0 | 0 |  | 1 | FALSE | wye
200008 | ипм | 318 | 210 | 70 | 0 | 0 |  | 1 | FALSE | wye
200009 | ТЮМЕНЬ | 4730 | 5000 | 50 | 0 | 0 |  | 1 | TRUE | wye
200010 | БЕРКУТ | 4728 | 298 | 10 | 0 | 0 |  | 1 | TRUE | wye
200011 | Троицкая грэс | 4798 | 50 | 25 | 0 | 0 |  | 1 | TRUE | wye
200012 | Есиль | 170 | 22 | -7 | 0 | 0 |  | 1 | TRUE | wye
200013 | РЕФТИНСКАЯ ГРЭС | 4702 | 550 | 150 | 0 | 0 |  | 1 | TRUE | wye
200014 | ЮЖНАЯ | 4701 | 10 | 5 | 0 | 0 |  | 1 | TRUE | wye
200015 | Кушмурун | 571 | 7 | 1 | 0 | 0 |  | 1 | FALSE | wye
200016 | Аман-карагай | 572 | 13 | 1 | 0 | 0 |  | 1 | FALSE | wye
200017 | Апановка | 573 | 33 | 4 | 0 | 0 |  | 1 | TRUE | wye
200018 | Лисаковка | 574 | 87 | -1 | 0 | 0 |  | 1 | TRUE | wye
200019 | Сокол-220 | 575 | 22 | 5 | 0 | 0 |  | 1 | TRUE | wye
200020 | Житикара-110 | 578 | 23 | 20 | 0 | 0 |  | 1 | TRUE | wye
200021 | ПРИВАЛОВСКАЯ | 50032 | 100 | 40 | 0 | 0 |  | 1 | TRUE | wye
200022 | ЗАРЯ | 1631 | 2500 | 200 | 0 | 0 |  | 1 | TRUE | wye
200023 | Качары | 582 | 24 | 16 | 0 | 0 |  | 1 | TRUE | wye
200024 | МАГНИТОГОРСКАЯ | 4785 | 614 | 400 | 0 | 0 |  | 1 | TRUE | wye
200025 | Челгаши | 585 | 7 | 1 | 0 | 0 |  | 1 | FALSE | wye
200026 | Центральная | 593 | 114 | 30 | 0 | 0 |  | 1 | TRUE | wye
200027 | ссгпо | 594 | 245 | 75 | 0 | 0 |  | 1 | TRUE | wye
200028 | Приуральская | 595 | 23 | 4 | 0 | 0 |  | 1 | TRUE | wye
200029 | ЗЛАТОУСТ | 4715 | 50 | 20 | 0 | 0 |  | 1 | TRUE | wye
200030 | УФИМСКАЯ | 4712 | 150 | 80 | 0 | 0 |  | 1 | TRUE | wye
200031 | Заречная | 596 | 27 | 3 | 0 | 0 |  | 1 | TRUE | wye
200032 | пс 51 | 251 | 19 | 4 | 0 | 0 |  | 1 | TRUE | wye
200033 | эгрэс-2-220 | 29 | 7 | -1 | 0 | 0 |  | 1 | TRUE | wye
200034 | еэк-20-бл5-8 | 30 | 43 | 11 | 0 | 0 |  | 1 | TRUE | wye
200035 | еэк-20-бл2-4 | 32 | 50 | 8 | 0 | 0 |  | 1 | TRUE | wye
200036 | еэк-220 | 33 | 1149 | 514 | 0 | 0 |  | 1 | TRUE | wye
200037 | Калкаман | 36 | 1 | 1 | 0 | 0 |  | 1 | TRUE | wye
200038 | нс-7 | 37 | 1 | 1 | 0 | 0 |  | 1 | FALSE | wye
200039 | Экибастуз-220 | 38 | 123 | 14 | 0 | 0 |  | 1 | TRUE | wye
200040 | эгрэс-1 | 39 | 52 | 21 | 0 | 0 |  | 1 | TRUE | wye
200041 | эгрэс-1-бл2 | 50 | 20 | 22 | 0 | 0 |  | 1 | TRUE | wye
200042 | эгрэс-1-бл3-8 | 51 | 92 | 40 | 0 | 0 |  | 1 | TRUE | wye
200043 | нс-12 | 52 | 1 | 1 | 0 | 0 |  | 1 | FALSE | wye
200044 | ээпк | 53 | 1 | 1 | 0 | 0 |  | 1 | TRUE | wye
200045 | црмз | 54 | 13 | 6 | 0 | 0 |  | 1 | TRUE | wye
200046 | азф | 55 | 429 | 230 | 0 | 0 |  | 1 | FALSE | wye
200047 | Строительная-2 | 56 | 7 | 2 | 0 | 0 |  | 1 | TRUE | wye
200048 | Уленты (т) | 58 | 9 | 3 | 0 | 0 |  | 1 | TRUE | wye
200049 | Бощак(T) | 59 | 8 | 3 | 0 | 0 |  | 1 | TRUE | wye
200050 | эгрэс-2-20 | 60 | 36 | 15 | 0 | 0 |  | 1 | TRUE | wye
200051 | Таскудык(Т) | 61 | 4 | 3 | 0 | 0 |  | 1 | TRUE | wye
200052 | нс 17 | 307 | 14 | 1 | 0 | 0 |  | 1 | FALSE | wye
200053 | Ерментау (т) | 166 | 3 | 2 | 0 | 0 |  | 1 | TRUE | wye
200054 | ИРТЫШСКАЯ | 1850 | 174 | 11 | 0 | 0 |  | 1 | TRUE | wye
200055 | КЭЗ-1.2 | 27 | 430 | 131 | 0 | 0 |  | 1 | TRUE | wye
200056 | пс-14 | 214 | 46 | 5 | 0 | 0 |  | 1 | TRUE | wye
200057 | пс-18 | 218 | 146 | 16 | 0 | 0 |  | 1 | TRUE | wye
200058 | шгэс-220 | 220 | 47 | 18 | 0 | 0 |  | 1 | TRUE | wye
200059 | жгок | 222 | 19 | -4 | 0 | 0 |  | 1 | TRUE | wye
200060 | Шоптыколь (т) | 101 | 10 | 6 | 0 | 0 |  | 1 | TRUE | wye
200061 | Батыс | 102 | 128 | 44 | 0 | 0 |  | 1 | TRUE | wye
200062 | Достык | 103 | 72 | 26 | 0 | 0 |  | 1 | TRUE | wye
200063 | Шыгыс | 104 | 0.4 | 0.2 | 0 | 0 |  | 1 | TRUE | wye
200064 | Осакаровка | 306 | 22 | 2 | 0 | 0 |  | 1 | TRUE | wye
200065 | Cарань | 308 | 1 | -11 | 0 | 0 |  | 1 | TRUE | wye
200066 | нс-19 | 309 | 23 | 4 | 0 | 0 |  | 1 | TRUE | wye
200067 | Нура-220 | 310 | 27 | 5 | 0 | 0 |  | 1 | TRUE | wye
200068 | грэс-2 | 355 | 260 | 150 | 0 | 0 |  | 1 | TRUE | wye
200069 | Кара-мурун | 450 | 5 | 1 | 0 | 0 |  | 1 | FALSE | wye
200070 | Жарык | 451 | 3 | 2 | 0 | 0 |  | 1 | FALSE | wye
200071 | Айса | 452 | 21 | 4 | 0 | 0 |  | 1 | TRUE | wye
200072 | Жана-арка | 453 | 6 | 2 | 0 | 0 |  | 1 | TRUE | wye
200073 | Барсенгир | 454 | 24 | -16 | 0 | 0 |  | 1 | TRUE | wye
200074 | Кумколь | 455 | 144 | 54.6 | 0 | 0 |  | 1 | TRUE | wye
200075 | Кайракты | 457 | 9 | 1 | 0 | 0 |  | 1 | TRUE | wye
200076 | Никольская | 461 | 53 | 39 | 0 | 0 |  | 1 | FALSE | wye
200077 | жтэц | 462 | 213 | 62 | 0 | 0 |  | 1 | FALSE | wye
200078 | жтэц-220 | 463 | 213 | 62 | 0 | 0 |  | 1 | TRUE | wye
200079 | Никольская | 464 | 56 | 45 | 0 | 0 |  | 1 | TRUE | wye
200080 | Kаражал | 465 | 19 | 5 | 0 | 0 |  | 1 | TRUE | wye
200081 | Aгадырь-220 | 468 | 17 | 2 | 0 | 0 |  | 1 | TRUE | wye
200082 | АГАДЫРЬ-500 | 469 | 10 | 0 | 0 | 0 |  | 1 | TRUE | wye
200083 | бтэц-110 | 471 | 111 | 58 | 0 | 0 |  | 1 | TRUE | wye
200084 | Балхашская-110 | 472 | 105 | -33 | 0 | 0 |  | 1 | TRUE | wye
200085 | Акчтау | 474 | 5 | -7 | 0 | 0 |  | 1 | TRUE | wye
200086 | Mоинты | 475 | 19 | 2 | 0 | 0 |  | 1 | TRUE | wye
200087 | Каражингил | 476 | 6 | 1 | 0 | 0 |  | 1 | FALSE | wye
200088 | Сарышаган | 477 | 6 | 2 | 0 | 0 |  | 1 | FALSE | wye
200089 | Мынарал | 924 | 2 | -3 | 0 | 0 |  | 1 | FALSE | wye
200090 | Кияхты | 930 | 6 | 3 | 0 | 0 |  | 1 | FALSE | wye
200091 | юкгрэс | 901 | 23 | -2 | 0 | 0 |  | 1 | TRUE | wye
200092 | Алматы | 903 | 10 | -7 | 0 | 0 |  | 1 | TRUE | wye
200093 | тэц-3 2сш | 904 | 220 | 50 | 0 | 0 |  | 1 | TRUE | wye
200094 | Робот | 907 | 37 | 2 | 0 | 0 |  | 1 | TRUE | wye
200095 | Бесагаш | 940 | 55 | -40 | 0 | 0 |  | 1 | TRUE | wye
200096 | пс-62 АТ2 | 908 | 18 | 14 | 0 | 0 |  | 1 | TRUE | wye
200097 | Чилик | 911 | 63 | 10 | 0 | 0 |  | 1 | TRUE | wye
200098 | пс-7 | 913 | 490 | 278 | 0 | 0 |  | 1 | TRUE | wye
200099 | Западная | 918 | 63 | 14 | 0 | 0 |  | 1 | TRUE | wye
200100 | Чиганак | 925 | 24 | 3 | 0 | 0 |  | 1 | TRUE | wye
200101 | Сары-Озек | 950 | 26 | 4 | 0 | 0 |  | 1 | TRUE | wye
200102 | Талдыкорганская-220 | 951 | 148 | 62 | 0 | 0 |  | 1 | TRUE | wye
200103 | Главная | 2916 | 680 | 18 | 0 | 0 |  | 1 | TRUE | wye
200104 | Медео | 928 | 10 | 1 | 0 | 0 |  | 1 | TRUE | wye
200105 | Таугуль | 929 | 202 | 38 | 0 | 0 |  | 1 | TRUE | wye
200106 | Жидели | 931 | 6 | 2 | 0 | 0 |  | 1 | FALSE | wye
200107 | Шу | 932 | 35 | 13 | 0 | 0 |  | 1 | TRUE | wye
200108 | Аспара | 814 | 5 | 1 | 0 | 0 |  | 1 | TRUE | wye
200109 | Жамбыл | 801 | 275 | 115 | 0 | 0 |  | 1 | TRUE | wye
200110 | Бурное | 802 | 10 | 5 | 0 | 0 |  | 1 | TRUE | wye
200111 | Каратау | 803 | 5 | -1 | 0 | 0 |  | 1 | TRUE | wye
200112 | Опорная | 804 | 16 | 5 | 0 | 0 |  | 1 | TRUE | wye
200113 | жгрэс-220 | 805 | 220 | 0 | 0 | 0 |  | 1 | TRUE | wye
200114 | жгрэс-16 | 806 | 7 | 1 | 0 | 0 |  | 1 | FALSE | wye
200115 | жгрэс-110 | 807 | 217 | 45 | 0 | 0 |  | 1 | FALSE | wye
200116 | Мерке | 809 | 5 | 1 | 0 | 0 |  | 1 | TRUE | wye
200117 | Жамбыл Тяга | 815 | 16 | 2 | 0 | 0 |  | 1 | TRUE | wye
200118 | Бурное Тяга | 816 | 14 | 6 | 0 | 0 |  | 1 | FALSE | wye
200119 | Абдезим | 817 | 5 | 1 | 0 | 0 |  | 1 | FALSE | wye
200120 | Шымкент-220 | 831 | 49 | 9 | 0 | 0 |  | 1 | TRUE | wye
200121 | Сас-тюбе | 834 | 8 | 2 | 0 | 0 |  | 1 | TRUE | wye
200122 | Ванновка | 835 | 10 | 3.477 | 0 | 0 |  | 1 | TRUE | wye
200123 | Бадам | 836 | 9 | 2 | 0 | 0 |  | 1 | FALSE | wye
200124 | Арысь | 837 | 7 | 1 | 0 | 0 |  | 1 | FALSE | wye
200125 | Монтайташ | 838 | 7 | 1 | 0 | 0 |  | 1 | FALSE | wye
200126 | Жылга | 839 | 29 | 9 | 0 | 0 |  | 1 | TRUE | wye
200127 | Кентау | 840 | 50 | 12 | 0 | 0 |  | 1 | TRUE | wye
200128 | Шолаккорган | 841 | 35 | -5 | 0 | 0 |  | 1 | TRUE | wye
200129 | Шымкентская | 843 | 150 | 50 | 0 | 0 |  | 1 | TRUE | wye
200130 | Тюлькубас | 844 | 3 | 2 | 0 | 0 |  | 1 | FALSE | wye
200131 | Кызылсай | 845 | 8 | 3 | 0 | 0 |  | 1 | TRUE | wye
200132 | Кызылординская тэц | 860 | 23 | 11 | 0 | 0 |  | 1 | TRUE | wye
200133 | Кызылординская | 862 | 23 | 6 | 0 | 0 |  | 1 | TRUE | wye
200134 | Шиели | 863 | 18 | 2 | 0 | 0 |  | 1 | TRUE | wye
200135 | Жанакорган | 865 | 6 | 2 | 0 | 0 |  | 1 | TRUE | wye
200136 | Жалагаш | 866 | 8 | 2 | 0 | 0 |  | 1 | FALSE | wye
200137 | Жусалы | 867 | 9 | 2.2642 | 0 | 0 |  | 1 | FALSE | wye
200138 | Бишкек | 2918 | 400 | 65 | 0 | 0 |  | 1 | TRUE | wye
200139 | ТАШ.ГРЭС | 2924 | 2500 | 0 | 0 | 0 |  | 1 | TRUE | wye
200140 | гпп-2 | 5957 | 97 | 4 | 0 | 0 |  | 1 | TRUE | wye
200141 | Ириклинская грэс | 4791 | 1140 | 50 | 0 | 0 |  | 1 | FALSE | wye
200142 | Таврическая | 1816 | 350 | -32 | 0 | 0 |  | 1 | TRUE | wye
200143 | Иртышская | 1851 | 159 | -10 | 0 | 0 |  | 1 | FALSE | wye
200144 | Миргалимсай | 842 | 20 | 13 | 0 | 0 |  | 1 | TRUE | wye
200145 | Сары-оба (т) | 169 | 3 | 2 | 0 | 0 |  | 1 | FALSE | wye
200146 | Еркеншилик (т) | 167 | 6 | 4 | 0 | 0 |  | 1 | TRUE | wye
200147 | Жолымбет | 123 | 27 | 6 | 0 | 0 |  | 1 | TRUE | wye
200148 | цгпп | 124 | 125 | -80 | 0 | 0 |  | 1 | TRUE | wye
200149 | Шортанды (т) | 125 | 11 | 1 | 0 | 0 |  | 1 | FALSE | wye
200150 | Танкерис (т) | 179 | 19 | 4 | 0 | 0 |  | 1 | TRUE | wye
200151 | Ельтай (т) | 178 | 4 | 2 | 0 | 0 |  | 1 | FALSE | wye
200152 | Бурабай (т) | 126 | 23 | 2 | 0 | 0 |  | 1 | TRUE | wye
200153 | Жалтыр (т) | 132 | 9 | 5 | 0 | 0 |  | 1 | TRUE | wye
200154 | Тастак (т) | 162 | 1 | 1 | 0 | 0 |  | 1 | FALSE | wye
200155 | Ирченко (т) | 163 | 1 | 1 | 0 | 0 |  | 1 | FALSE | wye
200156 | Атбасар | 134 | 43 | -28 | 0 | 0 |  | 1 | TRUE | wye
200157 | кгпп | 135 | 104 | 2 | 0 | 0 |  | 1 | TRUE | wye
200158 | Красноармейская | 159 | 17 | 3 | 0 | 0 |  | 1 | TRUE | wye
200159 | Киялы | 136 | 4 | 2 | 0 | 0 |  | 1 | TRUE | wye
200160 | БАРНАУЛ-500 | 1630 | 2500 | 200 | 0 | 0 |  | 1 | TRUE | wye
200161 | птэц-2-110 | 142 | 200 | 18 | 0 | 0 |  | 1 | TRUE | wye
200162 | птэц-2-220 | 144 | 4 | 2 | 0 | 0 |  | 1 | TRUE | wye
200163 | Актогай-110 | 484 | 22 | -13 | 0 | 0 |  | 1 | TRUE | wye
200164 | Аврора | 148 | 0 | 11 | 0 | 0 |  | 1 | TRUE | wye
200165 | ТУЛЕБЕРДЫЕВА | 2915 | 80 | 30 | 0 | 0 |  | 1 | FALSE | wye
200166 | Макинск | 150 | 22 | 2 | 0 | 0 |  | 1 | TRUE | wye
200167 | Степная | 151 | 124 | 31 | 0 | 0 |  | 1 | TRUE | wye
200168 | ТОКТОГУЛЬСКАЯ ГЭС | 2921 | 2230 | 55 | 0 | 0 |  | 1 | TRUE | wye
200169 | Янко (т) | 153 | 9 | 1 | 0 | 0 |  | 1 | TRUE | wye
200170 | Сибирь | 160 | 13 | 2 | 0 | 0 |  | 1 | FALSE | wye
200171 | Буран | 173 | 10 | 1 | 0 | 0 |  | 1 | TRUE | wye
200172 | Уголки(т) | 156 | 8 | 1 | 0 | 0 |  | 1 | TRUE | wye
200173 | Куйбышевская | 157 | 20 | -8 | 0 | 0 |  | 1 | TRUE | wye
200174 | Кокшетауская-1150 | 176 | 60 | -8 | 0 | 0 |  | 1 | TRUE | wye
200175 | Урожайная | 1673 | 150 | 60 | 0 | 0 |  | 1 | FALSE | wye
200176 | Перекатная (т) | 172 | 3 | 2 | 0 | 0 |  | 1 | TRUE | wye
200177 | Жаксы (т) | 164 | 1 | 1 | 0 | 0 |  | 1 | FALSE | wye
200178 | КУРГАН | 4727 | 500 | 200 | 0 | 0 |  | 1 | TRUE | wye
200179 | СМЕЛОВСКАЯ | 50014 | 350 | 80 | 0 | 0 |  | 1 | TRUE | wye
200180 | Экибастузская тэц | 44 | 41 | 5 | 0 | 0 |  | 1 | FALSE | wye
200181 | арбз | 4004 | 9 | 5 | 0 | 0 |  | 1 | FALSE | wye
200182 | бгок | 62 | 174 | 21 | 0 | 0 |  | 1 | TRUE | wye
200183 | Коян-Кос | 953 | 7 | 1 | 0 | 0 |  | 1 | TRUE | wye
200184 | Шымкентская ТЭЦ-3 | 813 | 220 | 42 | 0 | 0 |  | 1 | TRUE | wye
200185 | Барнаул-220 | 1640 | 320 | 92 | 0 | 0 |  | 1 | FALSE | wye
200186 | Ру-6 | 869 | 67 | 4 | 0 | 0 |  | 1 | TRUE | wye
200187 | УЗБЕКИСТОН | 2922 | 577 | 272 | 0 | 0 |  | 1 | FALSE | wye
200188 | АЛТАЙ | 1660 | 12500 | 5200 | 0 | 0 |  | 1 | TRUE | wye
200189 | СЫРДАРЬИНСКАЯ ТЭС | 2923 | 6390 | 3066 | 0 | 0 |  | 1 | FALSE | wye
200190 | Рубцовская | 1622 | 175 | 70 | 0 | 0 |  | 1 | TRUE | wye
200191 | ЛОЧИН | 2920 | 290 | 110 | 0 | 0 |  | 1 | FALSE | wye
200192 | БАРАБИНСКАЯ | 9917 | 135 | -40 | 0 | 0 |  | 1 | TRUE | wye
200193 | КУРЧАТОВСКАЯ | 50002 | 200 | 100 | 0 | 0 |  | 1 | TRUE | wye
200194 | сэс бурное | 810 | 1 | 1 | 0 | 0 |  | 1 | TRUE | wye
200195 | ЮЖНОУРАЛЬСКАЯ ГРЭС-2 | 47161 | 150 | 80 | 0 | 0 |  | 1 | TRUE | wye
200196 | Кемин | 2952 | 475 | 70 | 0 | 0 |  | 1 | TRUE | wye
200197 | Восход | 1854 | 213 | 56 | 0 | 0 |  | 1 | TRUE | wye
200198 | ВИТЯЗЬ | 1852 | 1 | 1 | 0 | 0 |  | 1 | TRUE | wye
200199 | КЕМИН | 2951 | 1200 | 500 | 0 | 0 |  | 1 | TRUE | wye
200200 | Акмолинская ТЭЦ | 108 | 140 | 0 | 0 | 0 |  | 1 | TRUE | wye
200201 | ДАТКА | 2950 | 200 | 100 | 0 | 0 |  | 1 | FALSE | wye
200202 | Акжар | 3004 | 9 | 5 | 0 | 0 |  | 1 | FALSE | wye
200203 | Ерменсай | 942 | 146 | -25 | 0 | 0 |  | 1 | TRUE | wye
200204 | ТМК | 242 | 79 | 30 | 0 | 0 |  | 1 | TRUE | wye
200205 | ПС-7 | 215 | 810 | 400 | 0 | 0 |  | 1 | TRUE | wye
200206 | Новокузнецкая | 1638 | 100 | 50 | 0 | 0 |  | 1 | FALSE | wye
200207 | Итатская | 1636 | 100 | 50 | 0 | 0 |  | 1 | FALSE | wye
200208 | Юрга | 1632 | 100 | 50 | 0 | 0 |  | 1 | FALSE | wye
200209 | Барабинская-220 | 1671 | 51 | 0 | 0 | 0 |  | 1 | FALSE | wye
200230 | ШАГОЛ | 4782 | 1282.7563 | 381.1 | 0 | 0 |  | 1 | TRUE | wye

## gen
| name | bus | p_mw | vm_pu | sn_mva | min_q_mvar | max_q_mvar | scaling | slack | in_service | slack_weight | type | power_station_trafo
300001 | Актюбе-220 | 3006 | 276 | 1 |  | 22 | 112 | 1 | FALSE | FALSE | 0
300002 | НОВО-АНГРЕНСКАЯ ТЭС | 2945 | 1778 | 1.11 |  | -300 | 1200 | 1 | FALSE | FALSE | 0
300003 | тэц-3 | 383 | 602 | 1.16 |  | -266 | 535 | 1 | FALSE | TRUE | 0
300004 | Металлургическая | 384 | 353 | 1.15 |  | -128 | 329 | 1 | FALSE | TRUE | 0
300005 | Ташкентская грэс | 2926 | 123 | 1.99 |  | -500 | 920 | 1 | FALSE | FALSE | 0
300006 | Чилисай | 3019 | 186 | 1.12 |  | 8 | 74 | 1 | FALSE | FALSE | 0
300007 | ТЮМЕНЬ | 4730 | 3760 | 1.13 |  | -1000 | 1000 | 1 | FALSE | TRUE | 0
300008 | ИРИКЛИНСКАЯ ГРЭС | 4790 | 474 | 1.11 |  | -200 | 200 | 1 | FALSE | TRUE | 0
300009 | ТРОИЦКАЯ ГРЭС | 4799 | 748 | 1.11 |  | -500 | 500 | 1 | FALSE | TRUE | 0
300010 | РЕФТИНСКАЯ ГРЭС | 4702 | 2850 | 1.12 |  | -1000 | 1050 | 1 | FALSE | TRUE | 0
300013 | ЗАРЯ | 1631 | 2857 | 1.12 |  | -1000 | 1000 | 1 | FALSE | TRUE | 0
300014 | МАГНИТОГОРСКАЯ | 4785 | 500 | 1.11 |  | -500 | 500 | 1 | FALSE | TRUE | 0
300015 | ссгпо | 594 | 94 | 1.14 |  | -58.5 | 112 | 1 | FALSE | TRUE | 0
300016 | ЧЕЛЯБИНСК | 4705 | 411.5013 | 1.11 |  |  |  | 1 | FALSE | TRUE | 0
300017 | еэк-20-бл5-8 | 30 | 587 | 1 |  | -113 | 387 | 1 | FALSE | TRUE | 0
300018 | еэк-20-бл2-4 | 32 | 916 | 1.97 |  | -117 | 603 | 1 | FALSE | TRUE | 0
300019 | еэк-220 | 33 | 925 | 1.17 |  | -33 | 967 | 1 | FALSE | TRUE | 0
300020 | Экибастуз-220 | 38 | 12 | 1.15 |  |  | 9 | 1 | FALSE | TRUE | 0
300021 | эгрэс-1-бл2 | 50 | 501 | 1 |  | -189.8 | 350.2 | 1 | FALSE | TRUE | 0
300022 | эгрэс-1-бл3-8 | 51 | 1784 | 1.11 |  | -567.3 | 1345.1 | 1 | FALSE | TRUE | 0
300023 | эгрэс-2-20 | 60 | 921 | 1.12 |  | -343.7 | 661.6 | 1 | FALSE | TRUE | 0
300024 | шгэс-14 | 221 | 152 | 1.13 |  | -210.1538 | 80.6154 | 1 | FALSE | TRUE | 0
300025 | грэс-2 | 355 | 508 | 1.15 |  | -80 | 417 | 1 | FALSE | TRUE | 0
300026 | Кумколь | 455 | 131 | 1.19 |  | -5.5 | 61 | 1 | FALSE | TRUE | 0
300027 | жтэц | 462 | 200 | 1.19 |  | -13 | 147 | 1 | FALSE | FALSE | 0
300028 | жтэц-220 | 463 | 200 | 1.17 |  | 25 | 235 | 1 | FALSE | TRUE | 0
300029 | бтэц-110 | 471 | 120 | 1.1 |  | 20 | 90 | 1 | FALSE | TRUE | 0
300030 | тэц-3 2сш | 904 | 169 | 1.16 |  | 20 | 160 | 1 | FALSE | TRUE | 0
300031 | Робот | 907 | 1 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300032 | Капчагайская гэс-220 | 909 | 89 | 1.19 |  |  | 112 | 1 | FALSE | TRUE | 0
300033 | Капчагайская гэс-14 | 910 | 89 | 1.14 |  |  | 112 | 1 | FALSE | FALSE | 0
300034 | Мойнакская гэс-15-1 | 937 | 146 | 1.12 |  | -11144 | 87992 | 1 | FALSE | FALSE | 0
300035 | пс-7 | 913 | 483 | 1.19 |  | 65 | 380 | 1 | FALSE | TRUE | 0
300036 | Талдыкорганская-220 | 951 | 40 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300037 | Главная | 2916 | 270 | 1.15 |  | -90 | 90 | 1 | FALSE | TRUE | 0
300038 | жгрэс-220 | 805 | 370 | 1.16 |  | 220 | 762 | 1 | FALSE | TRUE | 0
300039 | жгрэс-16 | 806 | 161 | 1 |  | -39 | 139.55 | 1 | FALSE | FALSE | 0
300040 | жгрэс-110 | 807 | 209 | 1.15 |  | -58 | 152 | 1 | FALSE | FALSE | 0
300041 | Кызылординская тэц | 860 | 52 | 1 |  | -31.6 | 67.3 | 1 | FALSE | TRUE | 0
300042 | ТАШ.ГРЭС | 2924 | 2864 | 1.12 |  | -1000 | 1000 | 1 | FALSE | TRUE | 0
300043 | Ташкент | 2925 | 123 | 1.99 |  | -500 | 960 | 1 | FALSE | TRUE | 0
300044 | Ириклинская грэс | 4791 | 227 | 1.1 |  | -400 | 300 | 1 | FALSE | FALSE | 0
300045 | БАРНАУЛ-500 | 1630 | 2523 | 1.11 |  | -1000 | 1000 | 1 | FALSE | TRUE | 0
300046 | птэц-2-110 | 142 | 295 | 1.17 |  | -134 | 346 | 1 | FALSE | TRUE | 0
300047 | птэц-2-220 | 144 | 172 | 1.12 |  | -64 | 152 | 1 | FALSE | TRUE | 0
300048 | Степная | 151 | 108 | 1.17 |  | 12 | 189 | 1 | FALSE | TRUE | 0
300049 | ТОКТОГУЛЬСКАЯ ГЭС | 2921 | 2360 | 1.14 |  | -800 | 800 | 1 | FALSE | TRUE | 0
300050 | КУРГАН | 4727 | 500 | 1.11 |  | -500 | 500 | 1 | FALSE | TRUE | 0
300051 | Экибастузская тэц | 44 | 12 | 1.97 |  |  | 9 | 1 | FALSE | FALSE | 0
300052 | арбз | 4004 | 40 | 1.15 |  | -10 | 20 | 1 | FALSE | FALSE | 0
300053 | wtu 2.0 | 191 | 6 | 1 |  | -5 | 5 | 1 | FALSE | FALSE | 0
300054 | Шымкентская ТЭЦ-3 | 813 | 57 | 1.18 |  | -105 | 185 | 1 | FALSE | TRUE | 0
300055 | Мойнакская гэс-220 | 935 | 146 | 1.11 |  | -24 | 202 | 1 | FALSE | TRUE | 0
300056 | АЛТАЙ | 1660 | 12865 | 1.11 |  | -6000 | 6000 | 1 | FALSE | TRUE | 0
300057 | СЫРДАРЬИНСКАЯ ТЭС | 2923 | 5240 | 1.11 |  | -2000 | 10300 | 1 | FALSE | FALSE | 0
300058 | КУРЧАТОВСКАЯ | 50002 | 850 | 1.13 |  | -60 | 60 | 1 | FALSE | TRUE | 0
300059 | вэс ерейментау | 155 | 6 | 1.16 |  | -5 | 5 | 1 | FALSE | TRUE | 0
300060 | ЮЖНОУРАЛЬСКАЯ ГРЭС-2 | 47161 | 250 | 1.13 |  | -300 | 300 | 1 | FALSE | TRUE | 0
300061 | КЕМИН | 2951 | 1454 | 1.14 |  | -800 | 800 | 1 | FALSE | TRUE | 0
300062 | Акмолинская ТЭЦ | 108 | 129 | 1.16 |  | -223.9 | 463.3 | 1 | FALSE | TRUE | 0
300063 | ДАТКА | 2950 | 1115 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300064 | Акжар | 3004 | 40 | 1.15 |  | -10 | 20 | 1 | FALSE | FALSE | 0
300065 | Ерменсай | 942 | 15 | 1.12 |  | -10 | 10 | 1 | FALSE | TRUE | 0
300066 | бтэц-10 | 470 | 120 | 1 |  | 20 | 90 | 1 | FALSE | FALSE | 0
300067 | ТМК | 242 | 50 | 1.14 |  | -291 | 404 | 1 | FALSE | TRUE | 0
300068 | ПС-7 | 215 | 845 | 1.14 |  | -110 | 256 | 1 | FALSE | TRUE | 0
300069 | Новокузнецкая | 1638 | 378 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300070 | Итатская | 1636 | 500 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300071 | Юрга | 1632 | 472 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300072 | Жана-арка | 453 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300073 | Барсенгир | 454 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300074 | Кумколь | 455 | 131 | 1.19 |  | -5.5 | 61 | 1 | FALSE | TRUE | 0
300075 | Кайракты | 457 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300076 | Никольская | 461 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300077 | жтэц | 462 | 200 | 1.19 |  | -13 | 147 | 1 | FALSE | FALSE | 0
300078 | жтэц-220 | 463 | 200 | 1.17 |  | 25 | 235 | 1 | FALSE | TRUE | 0
300079 | Никольская | 464 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300080 | Kаражал | 465 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300081 | Aгадырь-220 | 468 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300082 | АГАДЫРЬ-500 | 469 | 0 | 1.14 |  | -360 |  | 1 | FALSE | TRUE | 0
300083 | бтэц-110 | 471 | 120 | 1.1 |  | 20 | 90 | 1 | FALSE | TRUE | 0
300084 | Балхашская-110 | 472 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300085 | Акчтау | 474 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300086 | Mоинты | 475 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300087 | Каражингил | 476 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300088 | Сарышаган | 477 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300089 | Мынарал | 924 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300090 | Кияхты | 930 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300091 | юкгрэс | 901 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300092 | Алматы | 903 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300093 | тэц-3 2сш | 904 | 169 | 1.16 |  | 20 | 160 | 1 | FALSE | TRUE | 0
300094 | Робот | 907 | 1 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300095 | Бесагаш | 940 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300096 | пс-62 АТ2 | 908 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300097 | Чилик | 911 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300098 | пс-7 | 913 | 483 | 1.19 |  | 65 | 380 | 1 | FALSE | TRUE | 0
300099 | Западная | 918 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300100 | Чиганак | 925 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300101 | Сары-Озек | 950 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300102 | Талдыкорганская-220 | 951 | 40 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300103 | Главная | 2916 | 270 | 1.15 |  | -90 | 90 | 1 | FALSE | TRUE | 0
300104 | Медео | 928 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300105 | Таугуль | 929 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300106 | Жидели | 931 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300107 | Шу | 932 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300108 | Аспара | 814 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300109 | Жамбыл | 801 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300110 | Бурное | 802 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300111 | Каратау | 803 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300112 | Опорная | 804 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300113 | жгрэс-220 | 805 | 370 | 1.16 |  | 220 | 762 | 1 | FALSE | TRUE | 0
300114 | жгрэс-16 | 806 | 161 | 1 |  | -39 | 139.55 | 1 | FALSE | FALSE | 0
300115 | жгрэс-110 | 807 | 209 | 1.15 |  | -58 | 152 | 1 | FALSE | FALSE | 0
300116 | Мерке | 809 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300117 | Жамбыл Тяга | 815 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300118 | Бурное Тяга | 816 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300119 | Абдезим | 817 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300120 | Шымкент-220 | 831 | 0 | 1.16 |  | -100 | 35 | 1 | FALSE | TRUE | 0
300121 | Сас-тюбе | 834 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300122 | Ванновка | 835 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300123 | Бадам | 836 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300124 | Арысь | 837 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300125 | Монтайташ | 838 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300126 | Жылга | 839 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300127 | Кентау | 840 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300128 | Шолаккорган | 841 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300129 | Шымкентская | 843 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300130 | Тюлькубас | 844 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300131 | Кызылсай | 845 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300132 | Кызылординская тэц | 860 | 52 | 1 |  | -31.6 | 67.3 | 1 | FALSE | TRUE | 0
300133 | Кызылординская | 862 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300134 | Шиели | 863 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300135 | Жанакорган | 865 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300136 | Жалагаш | 866 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300137 | Жусалы | 867 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300138 | Бишкек | 2918 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300139 | ТАШ.ГРЭС | 2924 | 2864 | 1.12 |  | -1000 | 1000 | 1 | FALSE | TRUE | 0
300140 | гпп-2 | 5957 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300141 | Ириклинская грэс | 4791 | 227 | 1.1 |  | -400 | 300 | 1 | FALSE | FALSE | 0
300142 | Таврическая | 1816 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300143 | Иртышская | 1851 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300144 | Миргалимсай | 842 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300145 | Сары-оба (т) | 169 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300146 | Еркеншилик (т) | 167 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300147 | Жолымбет | 123 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300148 | цгпп | 124 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300149 | Шортанды (т) | 125 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300150 | Танкерис (т) | 179 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300151 | Ельтай (т) | 178 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300152 | Бурабай (т) | 126 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300153 | Жалтыр (т) | 132 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300154 | Тастак (т) | 162 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300155 | Ирченко (т) | 163 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300156 | Атбасар | 134 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300157 | кгпп | 135 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300158 | Красноармейская | 159 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300159 | Киялы | 136 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300160 | БАРНАУЛ-500 | 1630 | 2523 | 1.11 |  | -1000 | 1000 | 1 | FALSE | TRUE | 0
300161 | птэц-2-110 | 142 | 295 | 1.17 |  | -134 | 346 | 1 | FALSE | TRUE | 0
300162 | птэц-2-220 | 144 | 172 | 1.12 |  | -64 | 152 | 1 | FALSE | TRUE | 0
300163 | Актогай-110 | 484 | 0 | 1.15 |  | -50 | -2 | 1 | FALSE | TRUE | 0
300164 | Аврора | 148 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300165 | ТУЛЕБЕРДЫЕВА | 2915 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300166 | Макинск | 150 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300167 | Степная | 151 | 108 | 1.17 |  | 12 | 189 | 1 | FALSE | TRUE | 0
300168 | ТОКТОГУЛЬСКАЯ ГЭС | 2921 | 2360 | 1.14 |  | -800 | 800 | 1 | FALSE | TRUE | 0
300169 | Янко (т) | 153 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300170 | Сибирь | 160 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300171 | Буран | 173 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300172 | Уголки(т) | 156 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300173 | Куйбышевская | 157 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300174 | Кокшетауская-1150 | 176 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300175 | Урожайная | 1673 | 0 | 1.11 |  | -100 | 156 | 1 | FALSE | FALSE | 0
300176 | Перекатная (т) | 172 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300177 | Жаксы (т) | 164 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300178 | КУРГАН | 4727 | 500 | 1.11 |  | -500 | 500 | 1 | FALSE | TRUE | 0
300179 | СМЕЛОВСКАЯ | 50014 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300180 | Экибастузская тэц | 44 | 12 | 1.97 |  |  | 9 | 1 | FALSE | FALSE | 0
300181 | арбз | 4004 | 40 | 1.15 |  | -10 | 20 | 1 | FALSE | FALSE | 0
300182 | бгок | 62 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300183 | Коян-Кос | 953 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300184 | Шымкентская ТЭЦ-3 | 813 | 57 | 1.18 |  | -105 | 185 | 1 | FALSE | TRUE | 0
300185 | Барнаул-220 | 1640 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300186 | Ру-6 | 869 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300187 | УЗБЕКИСТОН | 2922 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300188 | АЛТАЙ | 1660 | 12865 | 1.11 |  | -6000 | 6000 | 1 | FALSE | TRUE | 0
300189 | СЫРДАРЬИНСКАЯ ТЭС | 2923 | 5240 | 1.11 |  | -2000 | 10300 | 1 | FALSE | FALSE | 0
300190 | Рубцовская | 1622 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300191 | ЛОЧИН | 2920 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300192 | БАРАБИНСКАЯ | 9917 | 0 | 1.13 |  | -180 |  | 1 | FALSE | TRUE | 0
300193 | КУРЧАТОВСКАЯ | 50002 | 850 | 1.13 |  | -60 | 60 | 1 | FALSE | TRUE | 0
300194 | сэс бурное | 810 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300195 | ЮЖНОУРАЛЬСКАЯ ГРЭС-2 | 47161 | 250 | 1.13 |  | -300 | 300 | 1 | FALSE | TRUE | 0
300196 | Кемин | 2952 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300197 | Восход | 1854 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300198 | ВИТЯЗЬ | 1852 | 0 | 1 |  |  |  | 1 | FALSE | TRUE | 0
300199 | КЕМИН | 2951 | 1454 | 1.14 |  | -800 | 800 | 1 | FALSE | TRUE | 0
300200 | Акмолинская ТЭЦ | 108 | 129 | 1.16 |  | -223.9 | 463.3 | 1 | FALSE | TRUE | 0
300201 | ДАТКА | 2950 | 1115 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300202 | Акжар | 3004 | 40 | 1.15 |  | -10 | 20 | 1 | FALSE | FALSE | 0
300203 | Ерменсай | 942 | 15 | 1.12 |  | -10 | 10 | 1 | FALSE | TRUE | 0
300204 | ТМК | 242 | 50 | 1.14 |  | -291 | 404 | 1 | FALSE | TRUE | 0
300205 | ПС-7 | 215 | 845 | 1.14 |  | -110 | 256 | 1 | FALSE | TRUE | 0
300206 | Новокузнецкая | 1638 | 378 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300207 | Итатская | 1636 | 500 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300208 | Юрга | 1632 | 472 | 1 |  |  |  | 1 | FALSE | FALSE | 0
300209 | Барабинская-220 | 1671 | 0 | 1 |  |  |  | 1 | FALSE | FALSE | 0

## shunt
| bus | name | q_mvar | p_mw | vn_kv | step | max_step | in_service
600001 | 481 | Коунрад-220 | 95.6902 | 0 | 220 | 1 | 1 | TRUE
600002 | 987 | ТАЛДЫКОРГАН-500 | 163.6367 | 0 | 500 | 1 | 1 | TRUE
600003 | 980 | СЕМЕЙ-500 | 327.6422 | 0 | 500 | 1 | 1 | TRUE
600004 | 4730 | ТЮМЕНЬ | 519.5758 | 0 | 500 | 1 | 1 | TRUE
600005 | 4728 | БЕРКУТ | 170.3575 | 0 | 500 | 1 | 1 | TRUE
600006 | 4790 | ИРИКЛИНСКАЯ ГРЭС | 167.853 | 0 | 500 | 1 | 1 | TRUE
600007 | 180 | ЕСИЛЬ | 485.6966 | 0 | 500 | 1 | 1 | TRUE
600008 | 175 | КОКЧЕТАВСКАЯ | 648.4076 | 0 | 500 | 1 | 1 | TRUE
600009 | 4703 | КОЗЫРЕВО | 164.4682 | 0 | 500 | 1 | 1 | TRUE
600010 | 4702 | РЕФТИНСКАЯ ГРЭС | 169.8453 | 0 | 500 | 1 | 1 | TRUE
600011 | 576 | СОКОЛ-500 | 168.6762 | 0 | 500 | 1 | 1 | TRUE
600012 | 577 | ЖИТИКАРА-500 | 164.5455 | 0 | 500 | 1 | 1 | TRUE
600013 | 9001 | УЛЬКЕ-500 | 0 | 0 | 500 | 1 | 1 | TRUE
600014 | 578 | Житикара-110 | 79.5877 | 0 | 110 | 1 | 1 | TRUE
600015 | 4782 | ШАГОЛ | 163.25 | 0 | 500 | 1 | 1 | TRUE
600016 | 1631 | ЗАРЯ | 168.5158 | 0 | 500 | 1 | 1 | TRUE
600017 | 590 | КОСТАНАЙСКАЯ | 331.1279 | 0 | 500 | 1 | 1 | TRUE
600018 | 4712 | УФИМСКАЯ | 169.783 | 0 | 500 | 1 | 1 | TRUE
600019 | 4705 | ЧЕЛЯБИНСК | 168.024 | 0 | 500 | 1 | 1 | TRUE
600020 | 25 | ЭГРЭС-1-500 | 525.7727 | 0 | 500 | 1 | 1 | TRUE
600021 | 26 | ЭКИБАСТУЗСКАЯ | 1034.2036 | 0 | 500 | 1 | 1 | TRUE
600022 | 129 | ЦГПП | 332.7996 | 0 | 500 | 1 | 1 | TRUE
600023 | 1621 | РУБЦОВСКАЯ | 329.4872 | 0 | 500 | 1 | 1 | TRUE
600024 | 1817 | ТАВРИЧЕСКАЯ | 174.9428 | 0 | 500 | 1 | 1 | TRUE
600025 | 455 | Кумколь | 19.6645 | 0 | 110 | 1 | 1 | TRUE
600026 | 457 | Кайракты | 0 | 0 | 220 | 1 | 1 | TRUE
600027 | 469 | АГАДЫРЬ-500 | 508.8332 | 0 | 500 | 1 | 1 | TRUE
600028 | 472 | Балхашская-110 | 0 | 0 | 110 | 1 | 1 | TRUE
600029 | 473 | Балхашская-220 | 0 | 0 | 220 | 1 | 1 | TRUE
600030 | 480 | ЖЕЗКАЗГАН-500 | 170.2955 | 0 | 500 | 1 | 1 | TRUE
600031 | 900 | ЮКГРЭС | 504.6347 | 0 | 500 | 1 | 1 | TRUE
600032 | 2919 | ФРУНЗЕ | 171.5807 | 0 | 500 | 1 | 1 | TRUE
600033 | 902 | АЛМАТЫ | 171.5481 | 0 | 500 | 1 | 1 | TRUE
600034 | 938 | АЛМА | 171.8494 | 0 | 500 | 1 | 1 | TRUE
600035 | 800 | ЖАМБЫЛ | 172.2409 | 0 | 500 | 1 | 1 | TRUE
600036 | 862 | Кызылординская | 19.134 | 0 | 220 | 1 | 1 | TRUE
600037 | 134 | Атбасар | 43.0212 | 0 | 220 | 1 | 1 | TRUE
600038 | 1630 | БАРНАУЛ-500 | 333.0627 | 0 | 500 | 1 | 1 | TRUE
600039 | 147 | АВРОРА | 339.8539 | 0 | 500 | 1 | 1 | TRUE
600040 | 150 | Макинск | 42.5778 | 0 | 220 | 1 | 1 | TRUE
600041 | 2921 | ТОКТОГУЛЬСКАЯ ГЭС | 177.9321 | 0 | 500 | 1 | 1 | TRUE
600042 | 4727 | КУРГАН | 166.5313 | 0 | 500 | 1 | 1 | TRUE
600043 | 9932 | ШУ | 334.7656 | 0 | 500 | 1 | 1 | TRUE
600044 | 2922 | УЗБЕКИСТОН | 0 | 0 | 500 | 1 | 1 | TRUE
600045 | 986 | АКТОГАЙ | 160.8552 | 0 | 500 | 1 | 1 | TRUE
600046 | 1660 | АЛТАЙ | 651.8439 | 0 | 500 | 1 | 1 | TRUE
600047 | 2920 | ЛОЧИН | 0 | 0 | 500 | 1 | 1 | TRUE
600048 | 9917 | БАРАБИНСКАЯ | 174.5397 | 0 | 500 | 1 | 1 | TRUE
600049 | 50002 | КУРЧАТОВСКАЯ | 169.887 | 0 | 500 | 1 | 1 | TRUE
600050 | 50001 | ИСЕТЬ | 165.128 | 0 | 500 | 1 | 1 | TRUE
600051 | 47161 | ЮЖНОУРАЛЬСКАЯ ГРЭС-2 | 0 | 0 | 500 | 1 | 1 | TRUE
600052 | 1853 | ВОСХОД | 344.1644 | 0 | 500 | 1 | 1 | TRUE
600053 | 1852 | ВИТЯЗЬ | 334.4773 | 0 | 500 | 1 | 1 | TRUE
600054 | 2951 | КЕМИН | 117.624 | 0 | 500 | 1 | 1 | TRUE
600055 | 2950 | ДАТКА | 0 | 0 | 500 | 1 | 1 | TRUE

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
47090 | BAZA | 4709 | 1.05 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
400001 | Новотроицк - Ульке-220 |  | 3103 | 3020 | 1 | 5.1 | 45.71 | 1.9239 | 0 | 10 | 1 | 1 | ol | FALSE
400002 | ЖИТИКАРА-500 - УЛЬКЕ-500 |  | 577 | 9001 | 1 | 16.54 | 149.4 | 5.7923 | 0 | 10 | 1 | 1 | ol | FALSE
400003 | Орская - Кимперсай |  | 3104 | 3005 | 1 | 8.39 | 36.72 | 0.71938 | 0 | 10 | 1 | 1 | ol | FALSE
400004 | Орская - Актюбе-220 |  | 3104 | 3006 | 1 | 16.68 | 73.02 | 1.4305 | 0 | 10 | 1 | 1 | ol | FALSE
400005 | НОВО-АНГРЕНСКАЯ ТЭС - СЫРДАРЬИНСКАЯ ТЭС |  | 2945 | 2923 | 1 | 4.18 | 38.2 | 1.5569 | 0 | 10 | 1 | 1 | ol | FALSE
400006 | Нура-220 - Металлургическая |  | 310 | 384 | 1 | 1.56 | 6.2 | 0.12923 | 0 | 10 | 1 | 1 | ol | TRUE
400007 | Атбасар - Ирченко (т) |  | 134 | 163 | 1 | 6.1 | 27.1 | 0.53221 | 0 | 10 | 1 | 1 | ol | FALSE
400008 | пс-18 - Семей-220 |  | 218 | 981 | 1 | 0.5 | 5.18 | 0.13369 | 0 | 10 | 1 | 1 | ol | TRUE
400009 | кгпп - Красноармейская |  | 135 | 159 | 1 | 5.8 | 25.9 | 0.5077 | 0 | 10 | 1 | 1 | ol | TRUE
400010 | Макинск - Степная |  | 150 | 151 | 1 | 14 | 55.6 | 1.1586 | 0 | 10 | 1 | 1 | ol | TRUE
400011 | гпп-1 - гпп-2 |  | 5958 | 5957 | 1 | 3.12 | 12.17 | 0.25656 | 0 | 10 | 1 | 1 | ol | FALSE
400012 | КОСТАНАЙСКАЯ - ЧЕЛЯБИНСК |  | 590 | 4705 | 1 | 4 | 75.3 | 4.52 | 0 | 10 | 1 | 1 | ol | TRUE
400013 | ТРОИЦКАЯ ГРЭС - СОКОЛ-500 |  | 4799 | 576 | 1 | 4.92 | 50 | 1.9799 | 0 | 10 | 1 | 1 | ol | TRUE
400014 | ИРИКЛИНСКАЯ ГРЭС - ЖИТИКАРА-500 |  | 4790 | 577 | 1 | 5.05 | 57.9 | 2.3046 | 0 | 10 | 1 | 1 | ol | TRUE
400015 | ЕСИЛЬ - СОКОЛ-500 |  | 180 | 576 | 1 | 8.8 | 80 | 3.3996 | 0 | 10 | 1 | 1 | ol | TRUE
400016 | СОКОЛ-500 - ЖИТИКАРА-500 |  | 576 | 577 | 1 | 4.7 | 53.5 | 2.1263 | 0 | 10 | 1 | 1 | ol | TRUE
400017 | КОСТАНАЙСКАЯ - СОКОЛ-500 |  | 590 | 576 | 1 | 1.3 | 13.6 | 0.50611 | 0 | 10 | 1 | 1 | ol | TRUE
400018 | Троицкая грэс - Приуральская |  | 4798 | 595 | 1 | 4.8 | 18.9 | 0.39693 | 0 | 10 | 1 | 1 | ol | TRUE
400019 | Новотроицк - Орская |  | 3103 | 3104 | 1 | 0.88 | 5.08 | 0.10409 | 0 | 10 | 1 | 1 | ol | FALSE
400020 | Рысаево - Новотроицк |  | 3102 | 3103 | 1 | 5.37 | 30.5 | 0.63662 | 0 | 10 | 1 | 1 | ol | FALSE
400021 | Ириклинская грэс - Орская |  | 4791 | 3104 | 1 | 4.38 | 25.24 | 0.51662 | 0 | 10 | 1 | 1 | ol | FALSE
400022 | Приуральская - Качары |  | 595 | 582 | 1 | 7.8 | 30.6 | 0.64012 | 0 | 10 | 1 | 1 | ol | TRUE
400023 | Качары - Сокол-220 |  | 582 | 575 | 1 | 5.1 | 19.6 | 0.38197 | 0 | 10 | 1 | 1 | ol | TRUE
400024 | Сокол-220 - Заречная |  | 575 | 596 | 1 | 8 | 35.6 | 0.69901 | 0 | 10 | 1 | 1 | ol | TRUE
400025 | Кустанайская - Центральная |  | 592 | 593 | 1 | 4.7 | 20.9 | 0.40998 | 0 | 10 | 1 | 1 | ol | TRUE
400026 | Кустанайская - Сокол-220 |  | 592 | 575 | 1 | 3.8 | 17.1 | 0.33518 | 0 | 10 | 1 | 1 | ol | TRUE
400027 | Сокол-220 - Лисаковка |  | 575 | 574 | 1 | 3.9 | 28 | 0.58251 | 0 | 10 | 1 | 1 | ol | TRUE
400028 | Лисаковка - Апановка |  | 574 | 573 | 1 | 5.51 | 21.3 | 0.44563 | 0 | 10 | 1 | 1 | ol | TRUE
400029 | Апановка - Сокол-220 |  | 573 | 575 | 1 | 6.4 | 24.6 | 0.51248 | 0 | 10 | 1 | 1 | ol | TRUE
400030 | Апановка - Кушмурун |  | 573 | 571 | 1 | 10.5 | 40.7 | 0.83397 | 0 | 10 | 1 | 1 | ol | FALSE
400031 | Аман-карагай - Кушмурун |  | 572 | 571 | 1 | 4.12 | 16 | 0.32468 | 0 | 10 | 1 | 1 | ol | FALSE
400032 | Кушмурун - Челгаши |  | 571 | 585 | 1 | 9.85 | 38.1 | 0.79259 | 0 | 10 | 1 | 1 | ol | FALSE
400033 | Есиль - Челгаши |  | 170 | 585 | 1 | 6.5 | 25 | 0.4902 | 0 | 10 | 1 | 1 | ol | FALSE
400034 | Кемин - Бишкек |  | 2952 | 2918 | 1 | 21.66 | 93.26 | 1.9064 | 0 | 10 | 1 | 1 | ol | TRUE
400035 | Ириклинская грэс - Орская |  | 4791 | 3104 | 1 | 4.38 | 25.24 | 0.51662 | 0 | 10 | 1 | 2 | ol | FALSE
400036 | Ириклинская грэс - Новотроицк |  | 4791 | 3103 | 1 | 5.57 | 32.05 | 0.65604 | 0 | 10 | 1 | 1 | ol | FALSE
400037 | Ириклинская грэс - Новотроицк |  | 4791 | 3103 | 1 | 2.11 | 22.57 | 0.91992 | 0 | 10 | 1 | 2 | ol | FALSE
400038 | Ириклинская грэс - Рысаево |  | 4791 | 3102 | 1 | 9.8 | 54.27 | 1.1392 | 0 | 10 | 1 | 1 | ol | FALSE
400039 | ЛОЧИН - ДАТКА |  | 2920 | 2950 | 1 | 2.69 | 26.82 | 1.0679 | 0 | 10 | 1 | 1 | ol | FALSE
400040 | Сокол-220 - ссгпо |  | 575 | 594 | 1 | 0.94 | 3.7 | 0.077668 | 0 | 10 | 1 | 1 | ol | TRUE
400041 | Сокол-220 - ссгпо |  | 575 | 594 | 1 | 0.94 | 3.7 | 0.077668 | 0 | 10 | 1 | 2 | ol | TRUE
400042 | ШАГОЛ - ЮЖНОУРАЛЬСКАЯ ГРЭС-2 |  | 4782 | 47161 | 1 | 1.78 | 25.87 | 1.278 | 0 | 10 | 1 | 1 | ol | TRUE
400043 | Бурное - сэс бурное |  | 802 | 810 | 1 | 4.37 | 17.43 | 0.35014 | 0 | 10 | 1 | 1 | ol | TRUE
400044 | ЭГРЭС-1-500 - ЭКИБАСТУЗСКАЯ |  | 25 | 26 | 1 | 0.31 | 3.81 | 0.15311 | 0 | 10 | 1 | 1 | ol | TRUE
400045 | ЭКИБАСТУЗСКАЯ - ЭГРЭС-2-500 |  | 26 | 28 | 1 | 0.81 | 11.75 | 0.33009 | 0 | 10 | 1 | 1 | ol | TRUE
400046 | ЭКИБАСТУЗСКАЯ - КОКЧЕТАВСКАЯ |  | 26 | 175 | 1 | 6.05 | 132.7 | 6.9646 | 0 | 10 | 1 | 1 | ol | TRUE
400047 | еэк-220 - азф |  | 33 | 55 | 1 | 0.4 | 3 | 0.11873 | 0 | 10 | 1 | 1 | ol | FALSE
400048 | еэк-220 - азф |  | 33 | 55 | 1 | 0.4 | 3 | 0.11873 | 0 | 10 | 1 | 2 | ol | FALSE
400049 | еэк-220 - пс 51 |  | 33 | 251 | 1 | 6 | 64.3 | 2.6006 | 0 | 10 | 1 | 1 | ol | TRUE
400050 | Калкаман - еэк-220 |  | 36 | 33 | 1 | 6.47 | 26.7 | 0.57582 | 0 | 10 | 1 | 1 | ol | TRUE
400051 | нс-7 - нс-12 |  | 37 | 52 | 1 | 8.03 | 31.7 | 0.66272 | 0 | 10 | 1 | 1 | ol | FALSE
400052 | Экибастуз-220 - црмз |  | 38 | 54 | 1 | 2.38 | 9.83 | 0.21199 | 0 | 10 | 1 | 1 | ol | TRUE
400053 | эгрэс-1 - эгрэс-2-220 |  | 39 | 29 | 1 | 2.4 | 10.6 | 0.20881 | 0 | 10 | 1 | 1 | ol | TRUE
400054 | эгрэс-1 - эгрэс-2-220 |  | 39 | 29 | 1 | 2.3 | 10.2 | 0.19958 | 0 | 10 | 1 | 2 | ol | TRUE
400055 | эгрэс-1 - нс-7 |  | 39 | 37 | 1 | 8.2 | 32.3 | 0.67641 | 0 | 10 | 1 | 1 | ol | FALSE
400056 | эгрэс-1 - Экибастуз-220 |  | 39 | 38 | 1 | 5.2 | 20.3 | 0.42494 | 0 | 10 | 1 | 1 | ol | TRUE
400057 | Уленты (т) - Бощак(T) |  | 58 | 59 | 1 | 4 | 17.5 | 0.34346 | 0 | 10 | 1 | 1 | ol | TRUE
400058 | Уленты (т) - Бощак(T) |  | 58 | 59 | 1 | 4.2 | 18.5 | 0.36256 | 0 | 10 | 1 | 2 | ol | TRUE
400059 | ээпк - Калкаман |  | 53 | 36 | 1 | 6.8 | 27 | 0.56468 | 0 | 10 | 1 | 1 | ol | TRUE
400060 | эгрэс-2-220 - Строительная-2 |  | 29 | 56 | 1 | 0.13 | 0.6 | 0.011777 | 0 | 10 | 1 | 1 | ol | TRUE
400061 | Таскудык(Т) - еэк-220 |  | 61 | 33 | 1 | 3.38 | 14.8 | 0.28982 | 0 | 10 | 1 | 1 | ol | FALSE
400062 | Строительная-2 - Таскудык(Т) |  | 56 | 61 | 1 | 9.85 | 43.14 | 0.84505 | 0 | 10 | 1 | 1 | ol | TRUE
400063 | Ерментау (т) - Уленты (т) |  | 166 | 58 | 1 | 4.6 | 20.6 | 0.40394 | 0 | 10 | 1 | 1 | ol | TRUE
400064 | КЭЗ-1.2 - ЕЭК-500 |  | 27 | 31 | 1 | 0.72 | 7.45 | 0.29666 | 0 | 10 | 1 | 1 | ol | TRUE
400065 | КЭЗ-1.2 - ЕЭК-500 |  | 27 | 31 | 1 | 0.72 | 7.43 | 0.29571 | 0 | 10 | 1 | 2 | ol | TRUE
400066 | ЭКИБАСТУЗСКАЯ - АЛТАЙ |  | 26 | 1660 | 1 | 14.79 | 212.33 | 9.1228 | 0 | 10 | 1 | 1 | ol | TRUE
400067 | РУБЦОВСКАЯ - УСТЬ-КАМЕНОГРСКАЯ-500 |  | 1621 | 240 | 1 | 4.34 | 44.02 | 1.7825 | 0 | 10 | 1 | 1 | ol | TRUE
400068 | Усть-Камногорская-220 - пс-14 |  | 241 | 214 | 1 | 5.19 | 20.42 | 0.40425 | 0 | 10 | 1 | 1 | ol | TRUE
400069 | Усть-Камногорская-220 - пс-14 |  | 241 | 214 | 1 | 5.19 | 20.42 | 0.40425 | 0 | 10 | 1 | 2 | ol | TRUE
400070 | ЧЕЛЯБИНСК - ЗЛАТОУСТ |  | 4705 | 4715 | 1 | 2.65 | 35.2 | 1.4165 | 0 | 10 | 1 | 1 | ol | TRUE
400071 | шгэс-220 - пс-14 |  | 220 | 214 | 1 | 2.07 | 21.23 | 0.86262 | 0 | 10 | 1 | 1 | ol | TRUE
400072 | ШАГОЛ - ЧЕЛЯБИНСК |  | 4782 | 4705 | 1 | 1.5 | 19 | 0.73211 | 0 | 10 | 1 | 1 | ol | TRUE
400073 | СМЕЛОВСКАЯ - БЕКЕТОВО |  | 50014 | 4709 | 1 | 8.8 | 81.8 | 2.9603 | 0 | 10 | 1 | 1 | ol | TRUE
400074 | пс 51 - Семей-220 |  | 251 | 981 | 1 | 3.89 | 40.67 | 1.4356 | 0 | 10 | 1 | 1 | ol | TRUE
400075 | шгэс-220 - Семей-220 |  | 220 | 981 | 1 | 3.91 | 27.45 | 1.0281 | 0 | 10 | 1 | 1 | ol | TRUE
400076 | Шоптыколь (т) - Осакаровка |  | 101 | 306 | 1 | 5.71 | 25.01 | 0.48988 | 0 | 10 | 1 | 1 | ol | TRUE
400077 | Шоптыколь (т) - Осакаровка |  | 101 | 306 | 1 | 5.81 | 25.44 | 0.49847 | 0 | 10 | 1 | 2 | ol | TRUE
400078 | нс 17 - нс-19 |  | 307 | 309 | 1 | 4.6 | 18.2 | 0.35014 | 0 | 10 | 1 | 1 | ol | FALSE
400079 | нс-19 - Осакаровка |  | 309 | 306 | 1 | 5.81 | 22.6 | 0.44563 | 0 | 10 | 1 | 1 | ol | TRUE
400080 | НУРА-500 - АГАДЫРЬ-500 |  | 325 | 469 | 1 | 6.86 | 79.4 | 3.1863 | 0 | 10 | 1 | 1 | ol | TRUE
400081 | грэс-2 - отпайка-4 |  | 355 | 314 | 1 | 6.5 | 25.5 | 0.50611 | 0 | 10 | 1 | 1 | ol | TRUE
400082 | грэс-2 - отпайка-5 |  | 355 | 315 | 1 | 6.5 | 25.5 | 0.50611 | 0 | 10 | 1 | 1 | ol | TRUE
400083 | грэс-2 - Кара-мурун |  | 355 | 450 | 1 | 4.4 | 17.4 | 0.35778 | 0 | 10 | 1 | 1 | ol | FALSE
400084 | грэс-2 - Жана-арка |  | 355 | 453 | 1 | 15 | 60.3 | 1.1682 | 0 | 10 | 1 | 1 | ol | TRUE
400085 | грэс-2 - Кайракты |  | 355 | 457 | 1 | 15.7 | 62.8 | 1.2185 | 0 | 10 | 1 | 1 | ol | TRUE
400086 | Кара-мурун - Жарык |  | 450 | 451 | 1 | 5.83 | 23 | 0.47428 | 0 | 10 | 1 | 1 | ol | FALSE
400087 | Жарык - Айса |  | 451 | 452 | 1 | 4.17 | 16.47 | 0.33932 | 0 | 10 | 1 | 1 | ol | FALSE
400088 | Айса - Aгадырь-220 |  | 452 | 468 | 1 | 3.61 | 14.26 | 0.2938 | 0 | 10 | 1 | 1 | ol | TRUE
400089 | жтэц - Никольская |  | 462 | 461 | 1 | 4.76 | 10.04 | 0.84034 | 0 | 10 | 1 | 1 | ol | FALSE
400090 | жтэц-220 - Жезказган-220 |  | 463 | 466 | 1 | 1.68 | 7.09 | 0.14483 | 0 | 10 | 1 | 1 | ol | TRUE
400091 | жтэц-220 - Жезказган-220 |  | 463 | 466 | 1 | 1.84 | 7.76 | 0.1582 | 0 | 10 | 1 | 2 | ol | TRUE
400092 | Никольская - Барсенгир |  | 464 | 454 | 1 | 10.9 | 42.1 | 0.87281 | 0 | 10 | 1 | 1 | ol | TRUE
400093 | Никольская - Жезказган-220 |  | 464 | 466 | 1 | 1.58 | 6.66 | 0.13652 | 0 | 10 | 1 | 1 | ol | TRUE
400094 | Kаражал - Барсенгир |  | 465 | 454 | 1 | 21.9 | 84.8 | 1.9153 | 0 | 10 | 1 | 1 | ol | TRUE
400095 | Kаражал - жтэц-220 |  | 465 | 463 | 1 | 26.9 | 104.7 | 2.2613 | 0 | 10 | 1 | 1 | ol | TRUE
400096 | Жезказган-220 - Кумколь |  | 466 | 467 | 1 | 23.45 | 98.96 | 2.0229 | 0 | 10 | 1 | 1 | ol | TRUE
400097 | Жезказган-220 - Кумколь |  | 466 | 467 | 1 | 22.98 | 96.97 | 1.9824 | 0 | 10 | 1 | 2 | ol | TRUE
400098 | Aгадырь-220 - Kаражал |  | 468 | 465 | 1 | 18.1 | 70.4 | 1.4356 | 0 | 10 | 1 | 1 | ol | TRUE
400099 | Aгадырь-220 - Балхашская-220 |  | 468 | 473 | 1 | 23.67 | 99.68 | 2.0375 | 0 | 10 | 1 | 1 | ol | TRUE
400100 | Aгадырь-220 - Mоинты |  | 468 | 475 | 1 | 12.8 | 54.2 | 1.1134 | 0 | 10 | 1 | 1 | ol | TRUE
400101 | АГАДЫРЬ-500 - ЮКГРЭС |  | 469 | 900 | 1 | 11.5 | 118.41 | 4.6065 | 0 | 10 | 1 | 1 | ol | TRUE
400102 | бтэц-110 - Балхашская-110 |  | 471 | 472 | 1 | 0.35 | 1.48 | 0.11968 | 0 | 10 | 1 | 1 | ol | TRUE
400103 | Балхашская-220 - Акчтау |  | 473 | 474 | 1 | 15.9 | 63.6 | 1.2322 | 0 | 10 | 1 | 1 | ol | TRUE
400104 | Акчтау - Кайракты |  | 474 | 457 | 1 | 8.96 | 36.1 | 0.72384 | 0 | 10 | 1 | 1 | ol | TRUE
400105 | Mоинты - Каражингил |  | 475 | 476 | 1 | 4.41 | 18.6 | 0.39248 | 0 | 10 | 1 | 1 | ol | FALSE
400106 | Каражингил - Сарышаган |  | 476 | 477 | 1 | 8.39 | 35.4 | 0.74644 | 0 | 10 | 1 | 1 | ol | FALSE
400107 | ЖЕЗКАЗГАН-500 - АГАДЫРЬ-500 |  | 480 | 469 | 1 | 12.6 | 123 | 4.8892 | 0 | 10 | 1 | 1 | ol | TRUE
400108 | ЮКГРЭС - АЛМАТЫ |  | 900 | 902 | 1 | 9.35 | 85 | 3.581 | 0 | 10 | 1 | 1 | ol | TRUE
400109 | ЮКГРЭС - АЛМА |  | 900 | 938 | 1 | 9.2 | 98.2 | 3.6542 | 0 | 10 | 1 | 1 | ol | TRUE
400110 | АЛМАТЫ - АЛМА |  | 902 | 938 | 1 | 1.8 | 19.5 | 0.72416 | 0 | 10 | 1 | 1 | ol | TRUE
400111 | Алма - Бесагаш |  | 939 | 940 | 1 | 4.2 | 23.5 | 0.83365 | 0 | 10 | 1 | 1 | ol | TRUE
400112 | Алма - Бесагаш |  | 939 | 940 | 1 | 4.2 | 23.5 | 0.83365 | 0 | 10 | 1 | 2 | ol | TRUE
400113 | Алма - тэц-3 2сш |  | 939 | 904 | 1 | 2.6 | 11.2 | 0.22027 | 0 | 10 | 1 | 1 | ol | TRUE
400114 | Алма - тэц-3 2сш |  | 939 | 904 | 1 | 1.5 | 10.7 | 0.226 | 0 | 10 | 1 | 2 | ol | TRUE
400115 | юкгрэс - Мынарал |  | 901 | 924 | 1 | 4.6 | 20.5 | 0.40425 | 0 | 10 | 1 | 1 | ol | FALSE
400116 | Алматы - Робот |  | 903 | 907 | 1 | 7.71 | 30.44 | 0.63662 | 0 | 10 | 1 | 1 | ol | TRUE
400117 | Алматы - Медео |  | 903 | 928 | 1 | 7.01 | 31.31 | 0.61434 | 0 | 10 | 1 | 1 | ol | TRUE
400118 | Алматы - тэц-3 2сш |  | 903 | 904 | 1 | 7 | 30.15 | 0.61752 | 0 | 10 | 1 | 1 | ol | TRUE
400119 | Алматы - Главная |  | 903 | 2916 | 1 | 19 | 82 | 1.6711 | 0 | 10 | 1 | 1 | ol | TRUE
400120 | Алма - Чилик |  | 939 | 911 | 1 | 12 | 52.7 | 1.032 | 0 | 10 | 1 | 1 | ol | TRUE
400121 | Робот - пс-62 АТ2 |  | 907 | 908 | 1 | 0.1 | 0.9 | 0.019735 | 0 | 10 | 1 | 1 | ol | TRUE
400122 | Робот - пс-62 АТ2 |  | 907 | 908 | 1 | 0.3 | 1.2 | 0.023555 | 0 | 10 | 1 | 2 | ol | TRUE
400123 | пс-62 АТ2 - Капчагайская гэс-220 |  | 908 | 909 | 1 | 0.8 | 5.42 | 0.11332 | 0 | 10 | 1 | 1 | ol | TRUE
400124 | пс-62 АТ2 - Капчагайская гэс-220 |  | 908 | 909 | 1 | 1.2 | 5.6 | 0.11045 | 0 | 10 | 1 | 2 | ol | TRUE
400125 | Капчагайская гэс-220 - Сары-Озек |  | 909 | 950 | 1 | 8 | 35.3 | 0.69232 | 0 | 10 | 1 | 1 | ol | TRUE
400126 | Капчагайская гэс-220 - Сары-Озек |  | 909 | 950 | 1 | 8 | 35.3 | 0.69201 | 0 | 10 | 1 | 2 | ol | TRUE
400127 | Талдыкорган-220 - Талдыкорганская-220 |  | 988 | 951 | 1 | 4.29 | 18.79 | 0.36797 | 0 | 10 | 1 | 1 | ol | TRUE
400128 | Талдыкорган-220 - Талдыкорганская-220 |  | 988 | 951 | 1 | 4.73 | 20.72 | 0.40585 | 0 | 10 | 1 | 2 | ol | TRUE
400129 | пс-7 - Западная |  | 912 | 918 | 1 | 5 | 20 | 0.4902 | 0 | 10 | 1 | 1 | ol | TRUE
400130 | Западная - Кемин |  | 918 | 2952 | 1 | 9.27 | 40.58 | 0.79495 | 0 | 10 | 1 | 1 | ol | TRUE
400131 | Чиганак - Кияхты |  | 925 | 930 | 1 | 6.528 | 29.17 | 0.57251 | 0 | 10 | 1 | 1 | ol | FALSE
400132 | тэц-3 2сш - Медео |  | 904 | 928 | 1 | 0.33 | 1.49 | 0.029285 | 0 | 10 | 1 | 1 | ol | TRUE
400133 | Алматы - Таугуль |  | 903 | 929 | 1 | 9.3 | 33.8 | 0.64235 | 0 | 10 | 1 | 1 | ol | TRUE
400134 | Алматы - Таугуль |  | 903 | 929 | 1 | 9.3 | 33.8 | 0.64235 | 0 | 10 | 1 | 2 | ol | TRUE
400135 | Кияхты - Жидели |  | 930 | 931 | 1 | 8.53 | 37.75 | 0.74166 | 0 | 10 | 1 | 1 | ol | FALSE
400136 | Жидели - Шу |  | 931 | 932 | 1 | 7.9 | 35.2 | 0.69073 | 0 | 10 | 1 | 1 | ol | FALSE
400137 | Шу - Аспара |  | 932 | 814 | 1 | 1.3 | 6 | 0.11777 | 0 | 10 | 1 | 1 | ol | TRUE
400138 | Шу - Главная |  | 932 | 2916 | 1 | 16.8 | 72 | 1.4961 | 0 | 10 | 1 | 1 | ol | TRUE
400139 | ЖАМБЫЛ - ФРУНЗЕ |  | 800 | 2919 | 1 | 6 | 69 | 2.5815 | 0 | 10 | 1 | 1 | ol | TRUE
400140 | Жамбыл - сэс бурное |  | 801 | 810 | 1 | 3.33 | 12.77 | 0.2621 | 0 | 10 | 1 | 1 | ol | TRUE
400141 | Жамбыл - Каратау |  | 801 | 803 | 1 | 7.66 | 29.88 | 0.60734 | 0 | 10 | 1 | 1 | ol | TRUE
400142 | Жамбыл - жгрэс-220 |  | 801 | 805 | 1 | 4.1 | 16.26 | 0.32054 | 0 | 10 | 1 | 1 | ol | TRUE
400143 | Жамбыл - Жамбыл Тяга |  | 801 | 815 | 1 | 2.88 | 11.42 | 0.22536 | 0 | 10 | 1 | 1 | ol | TRUE
400144 | Жамбыл - Бурное Тяга |  | 801 | 816 | 1 | 4.98 | 20.19 | 0.40171 | 0 | 10 | 1 | 1 | ol | FALSE
400145 | ШЫМКЕНТ-500 - ЖАМБЫЛ |  | 830 | 800 | 1 | 4.1 | 51.6 | 1.9481 | 0 | 10 | 1 | 1 | ol | TRUE
400146 | Ванновка - Бурное |  | 835 | 802 | 1 | 2.69 | 10.32 | 0.21772 | 0 | 10 | 1 | 1 | ol | TRUE
400147 | Каратау - Опорная |  | 803 | 804 | 1 | 8.39 | 33.411 | 0.69484 | 0 | 10 | 1 | 1 | ol | TRUE
400148 | жгрэс-220 - Аспара |  | 805 | 814 | 1 | 21.9 | 86.36 | 1.8182 | 0 | 10 | 1 | 1 | ol | TRUE
400149 | жгрэс-220 - Абдезим |  | 805 | 817 | 1 | 11.88 | 44.3 | 0.9944 | 0 | 10 | 1 | 1 | ol | FALSE
400150 | Мерке - Бишкек |  | 809 | 2918 | 1 | 3.14 | 12.22 | 0.25051 | 0 | 10 | 1 | 1 | ol | TRUE
400151 | Жамбыл Тяга - жгрэс-220 |  | 815 | 805 | 1 | 2.1 | 8.37 | 0.16406 | 0 | 10 | 1 | 1 | ol | TRUE
400152 | Абдезим - Мерке |  | 817 | 809 | 1 | 4.75 | 17.73 | 0.39789 | 0 | 10 | 1 | 1 | ol | FALSE
400153 | ШЫМКЕНТ-500 - ТАШ.ГРЭС |  | 830 | 2924 | 1 | 3 | 32.5 | 1.4483 | 0 | 10 | 1 | 1 | ol | TRUE
400154 | Шымкент-220 - Шымкентская ТЭЦ-3 |  | 831 | 813 | 1 | 2.41 | 9.49 | 0.19417 | 0 | 10 | 1 | 1 | ol | TRUE
400155 | Шымкент-220 - Бадам |  | 831 | 836 | 1 | 6.69 | 26.43 | 0.55513 | 0 | 10 | 1 | 1 | ol | FALSE
400156 | Шымкент-220 - Шымкентская |  | 831 | 843 | 1 | 1.72 | 10.75 | 0.24383 | 0 | 10 | 1 | 1 | ol | TRUE
400157 | Шымкент-220 - Кызылсай |  | 831 | 845 | 1 | 4.79 | 18.8 | 0.39852 | 0 | 10 | 1 | 1 | ol | TRUE
400158 | Шымкент-220 - гнпс |  | 831 | 846 | 1 | 5.22 | 20.06 | 0.42144 | 0 | 10 | 1 | 1 | ol | TRUE
400159 | Ванновка - Сас-тюбе |  | 835 | 834 | 1 | 3.898 | 15.012 | 0.3135 | 0 | 10 | 1 | 1 | ol | TRUE
400160 | Бадам - Арысь |  | 836 | 837 | 1 | 4.17 | 16.98 | 0.346 | 0 | 10 | 1 | 1 | ol | FALSE
400161 | Арысь - Монтайташ |  | 837 | 838 | 1 | 4.62 | 18.23 | 0.38165 | 0 | 10 | 1 | 1 | ol | FALSE
400162 | Монтайташ - Жылга |  | 838 | 839 | 1 | 4.48 | 17.71 | 0.37179 | 0 | 10 | 1 | 1 | ol | FALSE
400163 | Жылга - Ташкент |  | 839 | 2925 | 1 | 5.02 | 31.85 | 0.67768 | 0 | 10 | 1 | 1 | ol | TRUE
400164 | Кентау - Шолаккорган |  | 840 | 841 | 1 | 9.24 | 35.438 | 0.7473 | 0 | 10 | 1 | 1 | ol | TRUE
400165 | Шолаккорган - Опорная |  | 841 | 804 | 1 | 5.2 | 20.2 | 0.42431 | 0 | 10 | 1 | 1 | ol | TRUE
400166 | Миргалимсай - Кентау |  | 842 | 840 | 1 | 2.16 | 8.4 | 0.17221 | 0 | 10 | 1 | 1 | ol | TRUE
400167 | Жанакорган - Миргалимсай |  | 865 | 842 | 1 | 12.53 | 48.14 | 1.009 | 0 | 10 | 1 | 1 | ol | TRUE
400168 | Шымкентская - Жылга |  | 843 | 839 | 1 | 6.55 | 41.4 | 0.88904 | 0 | 10 | 1 | 1 | ol | TRUE
400169 | Шымкентская - Миргалимсай |  | 843 | 842 | 1 | 19.699 | 79.3 | 1.5096 | 0 | 10 | 1 | 1 | ol | TRUE
400170 | Шымкентская - Ташкент |  | 843 | 2925 | 1 | 8.58 | 52.04 | 1.1497 | 0 | 10 | 1 | 1 | ol | TRUE
400171 | Кызылсай - Тюлькубас |  | 845 | 844 | 1 | 6.23 | 25.26 | 0.50038 | 0 | 10 | 1 | 1 | ol | FALSE
400172 | Бурное Тяга - Тюлькубас |  | 816 | 844 | 1 | 6007 | 25.86 | 0.52871 | 0 | 10 | 1 | 1 | ol | FALSE
400173 | Сас-тюбе - Шымкент-220 |  | 834 | 831 | 1 | 6.876 | 26.449 | 0.55389 | 0 | 10 | 1 | 1 | ol | TRUE
400174 | гнпс - Кентау |  | 846 | 840 | 1 | 22.28 | 85.6 | 1.7978 | 0 | 10 | 1 | 1 | ol | TRUE
400175 | Кызылординская тэц - отпайка |  | 860 | 861 | 1 | 0.18 | 0.79 | 0.015915 | 0 | 10 | 1 | 1 | ol | FALSE
400176 | отпайка - Жалагаш |  | 861 | 866 | 1 | 7.78 | 30.41 | 0.61657 | 0 | 10 | 1 | 1 | ol | FALSE
400177 | Кызылординская - Ру-6 |  | 862 | 869 | 1 | 14.45 | 56.43 | 1.1889 | 0 | 10 | 1 | 1 | ol | TRUE
400178 | Ру-6 - Кентау |  | 869 | 840 | 1 | 21.97 | 85.81 | 1.8077 | 0 | 10 | 1 | 1 | ol | TRUE
400179 | Кызылординская - Кызылординская тэц |  | 862 | 860 | 1 | 1.05 | 4.09 | 0.083079 | 0 | 10 | 1 | 1 | ol | TRUE
400180 | Кызылординская - отпайка |  | 862 | 861 | 1 | 1.04 | 4.1 | 0.083079 | 0 | 10 | 1 | 1 | ol | TRUE
400181 | Шиели - Кызылординская |  | 863 | 862 | 1 | 11.55 | 45.11 | 1.1004 | 0 | 10 | 1 | 1 | ol | TRUE
400182 | Жалагаш - Жусалы |  | 866 | 867 | 1 | 7.2 | 28 | 0.56818 | 0 | 10 | 1 | 1 | ol | FALSE
400183 | Жусалы - гпп-1 |  | 867 | 5958 | 1 | 9.8 | 38.28 | 0.77604 | 0 | 10 | 1 | 1 | ol | FALSE
400184 | Коунрад-110 - бтэц-110 |  | 482 | 471 | 1 | 1.4 | 5.5 | 0.13719 | 0 | 10 | 1 | 1 | ol | FALSE
400185 | Батыс - Достык |  | 102 | 103 | 1 | 2352 | 11466 | 0.26858 | 0 | 10 | 1 | 1 | ol | TRUE
400186 | Батыс - Достык |  | 102 | 103 | 1 | 2.35 | 11.47 | 0.26865 | 0 | 10 | 1 | 2 | ol | TRUE
400187 | Достык - Шыгыс |  | 103 | 104 | 1 | 2.92 | 16.8 | 0.34384 | 0 | 10 | 1 | 1 | ol | TRUE
400188 | Достык - Шыгыс |  | 103 | 104 | 1 | 2.92 | 16.8 | 0.34377 | 0 | 10 | 1 | 2 | ol | TRUE
400189 | цгпп - Акмолинская ТЭЦ |  | 130 | 108 | 1 | 0.15 | 0.79 | 0.016552 | 0 | 10 | 1 | 1 | ol | TRUE
400190 | Шыгыс - Шоптыколь (т) |  | 104 | 101 | 1 | 3.19 | 6.95 | 0.14037 | 0 | 10 | 1 | 1 | ol | TRUE
400191 | Шыгыс - Шоптыколь (т) |  | 104 | 101 | 1 | 3.09 | 6.52 | 0.13178 | 0 | 10 | 1 | 2 | ol | TRUE
400192 | Чернозубовка - Куйбышевская |  | 186 | 157 | 1 | 8.52 | 30.62 | 0.58263 | 0 | 10 | 1 | 1 | ol | TRUE
400193 | ЦГПП - ЕСИЛЬ |  | 129 | 180 | 1 | 11.12 | 113.36 | 4.5486 | 0 | 10 | 1 | 1 | ol | TRUE
400194 | ЮЖНОУРАЛЬСКАЯ ГРЭС-2 - ТРОИЦКАЯ ГРЭС |  | 47161 | 4799 | 1 | 1.29 | 18.64 | 0.9648 | 0 | 10 | 1 | 1 | ol | TRUE
400195 | Есиль - оп-80 (т) |  | 170 | 165 | 1 | 4.1 | 18.3 | 0.35937 | 0 | 10 | 1 | 1 | ol | FALSE
400196 | оп-80 (т) - Жаксы (т) |  | 165 | 164 | 1 | 2.8 | 12.5 | 0.24574 | 0 | 10 | 1 | 1 | ol | FALSE
400197 | кгпп - Кокшетауская-1150 |  | 135 | 176 | 1 | 3.6 | 18.8 | 0.40935 | 0 | 10 | 1 | 1 | ol | FALSE
400198 | цгпп - Батыс |  | 130 | 102 | 1 | 3.48 | 19.46 | 0.39884 | 0 | 10 | 1 | 1 | ol | TRUE
400199 | цгпп - Батыс |  | 130 | 102 | 1 | 3.48 | 19.46 | 0.39884 | 0 | 10 | 1 | 2 | ol | TRUE
400200 | Степная - Жолымбет |  | 151 | 123 | 1 | 8 | 31.6 | 0.70028 | 0 | 10 | 1 | 1 | ol | TRUE
400201 | Атбасар - Жалтыр (т) |  | 134 | 132 | 1 | 11.5 | 51.5 | 1.0103 | 0 | 10 | 1 | 1 | ol | TRUE
400202 | цгпп - Жалтыр (т) |  | 130 | 132 | 1 | 11.4 | 51.1 | 1.002 | 0 | 10 | 1 | 1 | ol | TRUE
400203 | цгпп - Сары-оба (т) |  | 130 | 169 | 1 | 4.9 | 22.2 | 0.43608 | 0 | 10 | 1 | 1 | ol | FALSE
400204 | Атбасар - Перекатная (т) |  | 134 | 172 | 1 | 2.9 | 13.1 | 0.25688 | 0 | 10 | 1 | 1 | ol | TRUE
400205 | Жолымбет - цгпп |  | 123 | 130 | 1 | 7.8 | 32 | 0.63662 | 0 | 10 | 1 | 1 | ol | TRUE
400206 | птэц-2-220 - Смирново |  | 144 | 143 | 1 | 5.09 | 22.27 | 0.43615 | 0 | 10 | 1 | 1 | ol | TRUE
400207 | птэц-2-220 - Смирново |  | 144 | 143 | 1 | 5.02 | 21.96 | 0.43036 | 0 | 10 | 1 | 2 | ol | TRUE
400208 | Аврора - Макушино |  | 148 | 4781 | 1 | 17.7 | 79.1 | 1.5534 | 0 | 10 | 1 | 1 | ol | FALSE
400209 | Нура-220 - ипм |  | 310 | 318 | 1 | 3.4 | 13 | 0.28011 | 0 | 10 | 1 | 1 | ol | FALSE
400210 | АВРОРА - ТАВРИЧЕСКАЯ |  | 147 | 1817 | 1 | 11.47 | 87.78 | 3.4377 | 0 | 10 | 1 | 1 | ol | TRUE
400211 | Киялы - Аврора |  | 136 | 148 | 1 | 3.4 | 15.3 | 0.29953 | 0 | 10 | 1 | 1 | ol | TRUE
400212 | Макинск - Бурабай (т) |  | 150 | 126 | 1 | 4.4 | 16.5 | 0.35651 | 0 | 10 | 1 | 1 | ol | TRUE
400213 | Бурабай (т) - Кокшетауская-1150 |  | 126 | 176 | 1 | 12.4 | 51.5 | 1.0918 | 0 | 10 | 1 | 1 | ol | TRUE
400214 | цгпп - Танкерис (т) |  | 130 | 179 | 1 | 3.4 | 15.1 | 0.29539 | 0 | 10 | 1 | 1 | ol | TRUE
400215 | Шортанды (т) - Танкерис (т) |  | 125 | 179 | 1 | 3.7 | 16.4 | 0.32245 | 0 | 10 | 1 | 1 | ol | FALSE
400216 | Аврора - Сибирь |  | 148 | 161 | 1 | 10.3 | 36.9 | 0.63662 | 0 | 10 | 1 | 1 | ol | FALSE
400217 | Куйбышевская - Янко (т) |  | 157 | 153 | 1 | 7.5 | 29.1 | 0.59206 | 0 | 10 | 1 | 1 | ol | TRUE
400218 | Янко (т) - Буран |  | 153 | 173 | 1 | 4.3 | 16.5 | 0.33423 | 0 | 10 | 1 | 1 | ol | TRUE
400219 | Буран - Уголки(т) |  | 173 | 156 | 1 | 3.2 | 12.5 | 0.25465 | 0 | 10 | 1 | 1 | ol | TRUE
400220 | Кокшетауская-1150 - Уголки(т) |  | 176 | 156 | 1 | 3.6 | 13.5 | 0.28966 | 0 | 10 | 1 | 1 | ol | TRUE
400221 | Сибирь - птэц-2-110 |  | 160 | 142 | 1 | 19.8 | 47.2 | 1.0472 | 0 | 10 | 1 | 1 | ol | FALSE
400222 | Ирченко (т) - Жалтыр (т) |  | 163 | 132 | 1 | 5.5 | 24.4 | 0.4781 | 0 | 10 | 1 | 1 | ol | FALSE
400223 | Жаксы (т) - Перекатная (т) |  | 164 | 172 | 1 | 5.5 | 24.6 | 0.48319 | 0 | 10 | 1 | 1 | ol | FALSE
400224 | цгпп - Тастак (т) |  | 130 | 162 | 1 | 5.3 | 23.6 | 0.46314 | 0 | 10 | 1 | 1 | ol | FALSE
400225 | Тастак (т) - Жалтыр (т) |  | 162 | 132 | 1 | 6.1 | 27.5 | 0.5389 | 0 | 10 | 1 | 1 | ol | FALSE
400226 | Красноармейская - Киялы |  | 159 | 136 | 1 | 4.3 | 19.3 | 0.37974 | 0 | 10 | 1 | 1 | ol | TRUE
400227 | Шортанды (т) - Ельтай (т) |  | 125 | 178 | 1 | 8.2 | 36.6 | 0.71906 | 0 | 10 | 1 | 1 | ol | FALSE
400228 | Ельтай (т) - Макинск |  | 178 | 150 | 1 | 4.9 | 22.2 | 0.43608 | 0 | 10 | 1 | 1 | ol | FALSE
400229 | Еркеншилик (т) - Сары-оба (т) |  | 167 | 169 | 1 | 4.6 | 20.5 | 0.40171 | 0 | 10 | 1 | 1 | ol | FALSE
400230 | АВРОРА - КОКЧЕТАВСКАЯ |  | 147 | 175 | 1 | 5 | 49.9 | 1.9512 | 0 | 10 | 1 | 1 | ol | TRUE
400231 | АВРОРА - КУРГАН |  | 147 | 4727 | 1 | 9.37 | 84.1 | 3.1958 | 0 | 10 | 1 | 1 | ol | TRUE
400232 | Акмолинская ТЭЦ - Шыгыс |  | 108 | 104 | 1 | 3.51 | 19.37 | 0.40648 | 0 | 10 | 1 | 1 | ol | TRUE
400233 | Жамбыл - жгрэс-220 |  | 801 | 805 | 1 | 4.07 | 15.83 | 0.32436 | 0 | 10 | 1 | 2 | ol | TRUE
400234 | Акмолинская ТЭЦ - Шыгыс |  | 108 | 104 | 1 | 3.42 | 18.87 | 0.3963 | 0 | 10 | 1 | 2 | ol | TRUE
400235 | Мынарал - Сарышаган |  | 924 | 477 | 1 | 9.09 | 40.63 | 0.79737 | 0 | 10 | 1 | 1 | ol | FALSE
400236 | Жамбыл - Каратау |  | 801 | 803 | 1 | 8.15 | 32.31 | 0.63662 | 0 | 10 | 1 | 2 | ol | TRUE
400237 | ЗЛАТОУСТ - ПРИВАЛОВСКАЯ |  | 4715 | 50032 | 1 | 1 | 12.6 | 0.55068 | 0 | 10 | 1 | 1 | ol | TRUE
400238 | КУРГАН - ВИТЯЗЬ |  | 4727 | 1852 | 1 | 9.4 | 87.42 | 3.5469 | 0 | 10 | 1 | 1 | ol | TRUE
400239 | Талдыкорган-220 - Сары-Озек |  | 988 | 950 | 1 | 4.25 | 18.62 | 0.36478 | 0 | 10 | 1 | 2 | ol | TRUE
400240 | Коунрад-110 - бтэц-110 |  | 482 | 471 | 1 | 1.4 | 5.5 | 0.13719 | 0 | 10 | 1 | 2 | ol | FALSE
400241 | Ульке-220 - Акжар |  | 3020 | 3004 | 1 | 2.65 | 11.58 | 0.22696 | 0 | 10 | 1 | 1 | ol | FALSE
400242 | Талдыкорган-220 - Сары-Озек |  | 988 | 950 | 1 | 4.74 | 20.76 | 0.4068 | 0 | 10 | 1 | 1 | ol | TRUE
400243 | КРОПАЧЕВО - ПРИВАЛОВСКАЯ |  | 4714 | 50032 | 1 | 1.78 | 23.79 | 1.13 | 0 | 10 | 1 | 1 | ol | TRUE
400244 | УФИМСКАЯ - КРОПАЧЕВО |  | 4712 | 4714 | 1 | 2.37 | 36.08 | 1.3751 | 0 | 10 | 1 | 1 | ol | TRUE
400245 | АЛМА - ТАЛДЫКОРГАН-500 |  | 938 | 987 | 1 | 5.91 | 62.76 | 2.3351 | 0 | 10 | 1 | 1 | ol | TRUE
400246 | БЕКЕТОВО - УФИМСКАЯ |  | 4709 | 4712 | 1 | 1.36 | 20.67 | 0.78941 | 0 | 10 | 1 | 1 | ol | TRUE
400247 | МАГНИТОГОРСКАЯ - СМЕЛОВСКАЯ |  | 4785 | 50014 | 1 | 0.64 | 5.9 | 0.22282 | 0 | 10 | 1 | 1 | ol | TRUE
400248 | юкгрэс - Чиганак |  | 901 | 925 | 1 | 0.98 | 4.3 | 0.082761 | 0 | 10 | 1 | 1 | ol | TRUE
400249 | Актюбе-220 - Ульке-220 |  | 3006 | 3020 | 1 | 4.94 | 17.7 | 0.34568 | 0 | 10 | 1 | 1 | ol | FALSE
400250 | Кимперсай - Акжар |  | 3005 | 3004 | 1 | 7.23 | 31.66 | 0.62007 | 0 | 10 | 1 | 1 | ol | FALSE
400251 | Актюбе-220 - Акжар |  | 3006 | 3004 | 1 | 1.4 | 6.13 | 0.12032 | 0 | 10 | 1 | 1 | ol | FALSE
400252 | Кумколь - гпп-2 |  | 467 | 5957 | 1 | 26.41 | 104.2 | 2.1792 | 0 | 10 | 1 | 1 | ol | TRUE
400253 | ЭКИБАСТУЗСКАЯ - ЭГРЭС-2-500 |  | 26 | 28 | 1 | 0.93 | 11.27 | 0.3129 | 0 | 10 | 1 | 2 | ol | TRUE
400254 | ЭГРЭС-1-500 - ЭКИБАСТУЗСКАЯ |  | 25 | 26 | 1 | 0.25 | 3.15 | 0.1264 | 0 | 10 | 1 | 2 | ol | TRUE
400255 | Жана-арка - Kаражал |  | 453 | 465 | 1 | 10.6 | 43 | 0.82601 | 0 | 10 | 1 | 1 | ol | TRUE
400256 | цгпп - Акмолинская ТЭЦ |  | 130 | 108 | 1 | 0.25 | 1.28 | 0.026738 | 0 | 10 | 1 | 2 | ol | TRUE
400257 | ЭГРЭС-1-500 - ЦГПП |  | 25 | 129 | 1 | 7.3 | 89.75 | 3.3795 | 0 | 10 | 1 | 1 | ol | TRUE
400258 | эгрэс-1 - бгок |  | 39 | 62 | 1 | 5.17 | 33.19 | 0.76299 | 0 | 10 | 1 | 1 | ol | TRUE
400259 | Смирново - Аврора |  | 143 | 148 | 1 | 0.75 | 3.26 | 0.06398 | 0 | 10 | 1 | 1 | ol | TRUE
400260 | вэс ерейментау - Ерментау (т) |  | 155 | 166 | 1 | 1.7 | 7.7 | 0.1512 | 0 | 10 | 1 | 1 | ol | TRUE
400261 | Еркеншилик (т) - вэс ерейментау |  | 167 | 155 | 1 | 5.05 | 22.57 | 0.44286 | 0 | 10 | 1 | 1 | ol | TRUE
400262 | Смирново - Аврора |  | 143 | 148 | 1 | 0.79 | 3.44 | 0.067482 | 0 | 10 | 1 | 2 | ol | TRUE
400263 | црмз - ээпк |  | 54 | 53 | 1 | 1.84 | 7.59 | 0.16361 | 0 | 10 | 1 | 1 | ol | TRUE
400264 | Коян-Кос - тэц-3 2сш |  | 953 | 904 | 1 | 0.85 | 4.75 | 0.097085 | 0 | 10 | 1 | 1 | ol | TRUE
400265 | Коян-Кос - тэц-3 2сш |  | 953 | 904 | 1 | 0.85 | 4.75 | 0.097085 | 0 | 10 | 1 | 2 | ol | TRUE
400266 | пс-7 - Коян-Кос |  | 912 | 953 | 1 | 1.13 | 6.3 | 0.12892 | 0 | 10 | 1 | 1 | ol | TRUE
400267 | пс-7 - Коян-Кос |  | 912 | 953 | 1 | 1.13 | 6.3 | 0.12892 | 0 | 10 | 1 | 2 | ol | TRUE
400268 | Робот - Алма |  | 907 | 939 | 1 | 2.1 | 14.2 | 0.29889 | 0 | 10 | 1 | 1 | ol | TRUE
400269 | АГАДЫРЬ-500 - ЮКГРЭС |  | 469 | 900 | 1 | 12.7 | 115.6 | 4.8574 | 0 | 10 | 1 | 2 | ol | TRUE
400270 | ЕЭК-500 - ЭГРЭС-1-500 |  | 31 | 25 | 1 | 3.05 | 36.64 | 1.4731 | 0 | 10 | 1 | 1 | ol | TRUE
400271 | нс-12 - нс 17 |  | 52 | 307 | 1 | 8.15 | 32.16 | 0.67291 | 0 | 10 | 1 | 1 | ol | FALSE
400272 | Шымкент-220 - Шымкентская ТЭЦ-3 |  | 831 | 813 | 1 | 2.41 | 9.49 | 0.19417 | 0 | 10 | 1 | 2 | ol | TRUE
400273 | Cарань - грэс-2 |  | 308 | 355 | 1 | 3.89 | 15.24 | 0.30558 | 0 | 10 | 1 | 1 | ol | TRUE
400274 | Главная - Чуйская |  | 2916 | 2932 | 1 | 5.87 | 25.28 | 0.51671 | 0 | 10 | 1 | 1 | ol | FALSE
400275 | Cарань - грэс-2 |  | 308 | 355 | 1 | 3.89 | 15.24 | 0.30558 | 0 | 10 | 1 | 2 | ol | TRUE
400276 | Осакаровка - Cарань |  | 306 | 308 | 1 | 9.81 | 38.36 | 0.77349 | 0 | 10 | 1 | 1 | ol | TRUE
400277 | Осакаровка - Cарань |  | 306 | 308 | 1 | 9.81 | 38.36 | 0.77349 | 0 | 10 | 1 | 2 | ol | TRUE
400278 | ЕЭК-500 - РУБЦОВСКАЯ |  | 31 | 1621 | 1 | 10.25 | 98.5 | 4.1062 | 0 | 10 | 1 | 1 | ol | TRUE
400279 | ДАТКА - КЕМИН |  | 2950 | 2951 | 1 | 9.72 | 120.63 | 4.9402 | 0 | 10 | 1 | 1 | ol | FALSE
400280 | ДАТКА - ТОКТОГУЛЬСКАЯ ГЭС |  | 2950 | 2921 | 1 | 2.4 | 23.92 | 0.95493 | 0 | 10 | 1 | 1 | ol | FALSE
400281 | ИСЕТЬ - КОЗЫРЕВО |  | 50001 | 4703 | 1 | 4.05 | 41.19 | 1.6552 | 0 | 10 | 1 | 1 | ol | TRUE
400282 | ЕЭК-500 - ИРТЫШСКАЯ |  | 31 | 1850 | 1 | 7.62 | 76.8 | 3.0335 | 0 | 10 | 1 | 1 | ol | TRUE
400283 | КУРЧАТОВСКАЯ - ШАГОЛ |  | 50002 | 4782 | 1 | 4.42 | 68.2 | 2.6028 | 0 | 10 | 1 | 1 | ol | TRUE
400284 | Апановка - Аман-карагай |  | 573 | 572 | 1 | 6.6 | 25.4 | 0.51885 | 0 | 10 | 1 | 1 | ol | FALSE
400285 | ЗАРЯ - БАРАБИНСКАЯ |  | 1631 | 9917 | 1 | 10.8 | 110 | 4.3784 | 0 | 10 | 1 | 1 | ol | TRUE
400286 | грэс-2 - Коунрад-220 |  | 355 | 481 | 1 | 34.2 | 146.2 | 3.0029 | 0 | 10 | 1 | 1 | ol | TRUE
400287 | РУБЦОВСКАЯ - БАРНАУЛ-500 |  | 1621 | 1630 | 1 | 10.3 | 105 | 4.364 | 0 | 10 | 1 | 1 | ol | TRUE
400288 | Бесагаш - Ерменсай |  | 940 | 942 | 1 | 1 | 5.4 | 4.4761 | 0 | 10 | 1 | 1 | ol | FALSE
400289 | Бесагаш - Ерменсай |  | 940 | 942 | 1 | 1 | 5.4 | 4.4761 | 0 | 10 | 1 | 2 | ol | TRUE
400290 | Нура-220 - ипм |  | 310 | 318 | 1 | 3.4 | 13 | 0.28011 | 0 | 10 | 1 | 2 | ol | FALSE
400291 | БАРНАУЛ-500 - АЛТАЙ |  | 1630 | 1660 | 1 | 0.26 | 2.64 | 0.10536 | 0 | 10 | 1 | 1 | ol | TRUE
400292 | БАРНАУЛ-500 - АЛТАЙ |  | 1630 | 1660 | 1 | 0.19 | 1.97 | 0.078623 | 0 | 10 | 1 | 2 | ol | TRUE
400293 | тэц-3 - ипм |  | 383 | 318 | 1 | 0.3 | 1.3 | 0.025465 | 0 | 10 | 1 | 2 | ol | FALSE
400294 | тэц-3 - ипм |  | 383 | 318 | 1 | 0.3 | 1.3 | 0.025465 | 0 | 10 | 1 | 1 | ol | FALSE
400295 | ЭКИБАСТУЗСКАЯ - СЕМЕЙ-500 |  | 26 | 980 | 1 | 10.1 | 122.52 | 4.8504 | 0 | 10 | 1 | 1 | ol | TRUE
400296 | Чуйская - Кемин |  | 2932 | 2952 | 1 | 5.77 | 24.85 | 0.5079 | 0 | 10 | 1 | 1 | ol | FALSE
400297 | пс-18 - Семей-220 |  | 218 | 981 | 1 | 0.37 | 3.88 | 0.10027 | 0 | 10 | 1 | 2 | ol | TRUE
400298 | СЕМЕЙ-500 - АКТОГАЙ |  | 980 | 986 | 1 | 9.84 | 120.42 | 4.5346 | 0 | 10 | 1 | 1 | ol | TRUE
400299 | грэс-2 - Коунрад-220 |  | 355 | 481 | 1 | 34.2 | 146.2 | 3.0029 | 0 | 10 | 1 | 2 | ol | TRUE
400300 | СЕМЕЙ-500 - УСТЬ-КАМЕНОГРСКАЯ-500 |  | 980 | 240 | 1 | 5.72 | 58.55 | 2.2944 | 0 | 10 | 1 | 1 | ol | TRUE
400301 | шгэс-220 - Семей-220 |  | 220 | 981 | 1 | 2.57 | 25.36 | 1.1077 | 0 | 10 | 1 | 2 | ol | TRUE
400302 | АКТОГАЙ - ТАЛДЫКОРГАН-500 |  | 986 | 987 | 1 | 8.33 | 88.52 | 3.2936 | 0 | 10 | 1 | 1 | ol | TRUE
400303 | БЕРКУТ - ТЮМЕНЬ |  | 4728 | 4730 | 1 | 1.28 | 11.38 | 0.31831 | 0 | 10 | 1 | 1 | ol | TRUE
400304 | КУРГАН - БЕРКУТ |  | 4727 | 4728 | 1 | 5 | 46.8 | 1.8526 | 0 | 10 | 1 | 1 | ol | TRUE
400305 | Нура-220 - Металлургическая |  | 310 | 384 | 1 | 1.56 | 6.2 | 0.12923 | 0 | 10 | 1 | 2 | ol | TRUE
400306 | Металлургическая - отпайка-5 |  | 384 | 315 | 1 | 2.65 | 10.4 | 0.20658 | 0 | 10 | 1 | 1 | ol | TRUE
400307 | Мойнакская гэс-220 - Робот |  | 935 | 907 | 1 | 17.1 | 95.7 | 1.9576 | 0 | 10 | 1 | 1 | ol | TRUE
400308 | тэц-3 - отпайка-5 |  | 383 | 315 | 1 | 0.2 | 0.9 | 0.018462 | 0 | 10 | 1 | 1 | ol | TRUE
400309 | Мойнакская гэс-220 - Чилик |  | 935 | 911 | 1 | 7.3 | 40.9 | 0.83716 | 0 | 10 | 1 | 1 | ol | TRUE
400310 | Таугуль - Ерменсай |  | 929 | 942 | 1 | 1.4 | 5.1 | 0.097403 | 0 | 10 | 1 | 1 | ol | TRUE
400311 | Таугуль - Ерменсай |  | 929 | 942 | 1 | 1.4 | 5.1 | 0.097403 | 0 | 10 | 1 | 2 | ol | TRUE
400312 | ВИТЯЗЬ - ВОСХОД |  | 1852 | 1853 | 1 | 8.56 | 102.65 | 4.1501 | 0 | 10 | 1 | 1 | ol | TRUE
400313 | ВОСХОД - ТАВРИЧЕСКАЯ |  | 1853 | 1817 | 1 | 2.1 | 21.85 | 0.8709 | 0 | 10 | 1 | 1 | ol | TRUE
400314 | ВОСХОД - БАРАБИНСКАЯ |  | 1853 | 9917 | 1 | 8.43 | 86.95 | 3.4619 | 0 | 10 | 1 | 1 | ol | TRUE
400315 | шгэс-220 - жгок |  | 220 | 222 | 1 | 8.76 | 30.8 | 0.64458 | 0 | 10 | 1 | 1 | ol | TRUE
400316 | Металлургическая - отпайка-4 |  | 384 | 314 | 1 | 2.65 | 10.4 | 0.20658 | 0 | 10 | 1 | 1 | ol | TRUE
400317 | АЛТАЙ - ЗАРЯ |  | 1660 | 1631 | 1 | 5.46 | 50.12 | 2.1072 | 0 | 10 | 1 | 1 | ol | TRUE
400318 | тэц-3 - отпайка-4 |  | 383 | 314 | 1 | 0.2 | 0.9 | 0.018462 | 0 | 10 | 1 | 1 | ol | TRUE
400319 | МАГНИТОГОРСКАЯ - ТРОИЦКАЯ ГРЭС |  | 4785 | 4799 | 1 | 6.2 | 54.6 | 2.4351 | 0 | 10 | 1 | 1 | ol | TRUE
400320 | КОЗЫРЕВО - ШАГОЛ |  | 4703 | 4782 | 1 | 1.96 | 16.2 | 0.69392 | 0 | 10 | 1 | 1 | ol | TRUE
400321 | ИРИКЛИНСКАЯ ГРЭС - МАГНИТОГОРСКАЯ |  | 4790 | 4785 | 1 | 6.8 | 66 | 2.7056 | 0 | 10 | 1 | 1 | ol | TRUE
400322 | Урожайная - Барнаул-220 |  | 1673 | 1640 | 1 | 26.5 | 103.7 | 8.362 | 0 | 10 | 1 | 1 | ol | FALSE
400323 | Заречная - Центральная |  | 596 | 593 | 1 | 0.8 | 3.66 | 0.071938 | 0 | 10 | 1 | 1 | ol | TRUE
400324 | Чилисай - Ульке-220 |  | 3019 | 3020 | 1 | 17.1 | 61.47 | 1.1695 | 0 | 10 | 1 | 1 | ol | FALSE
400325 | Есиль - Чернозубовка |  | 170 | 186 | 1 | 12.39 | 44.54 | 0.84747 | 0 | 10 | 1 | 1 | ol | TRUE
400326 | КОКЧЕТАВСКАЯ - КОСТАНАЙСКАЯ |  | 175 | 590 | 1 | 5.02 | 106.96 | 5.5609 | 0 | 10 | 1 | 1 | ol | TRUE
400327 | АГАДЫРЬ-500 - ЭКИБАСТУЗСКАЯ |  | 469 | 26 | 1 | 11.6 | 138.3 | 5.594 | 0 | 10 | 1 | 1 | ol | TRUE
400328 | эгрэс-1 - Бощак(T) |  | 39 | 59 | 1 | 9.69 | 40.78 | 0.87854 | 0 | 10 | 1 | 1 | ol | TRUE
400329 | эгрэс-1 - Бощак(T) |  | 39 | 59 | 1 | 7.88 | 34.5 | 0.67609 | 0 | 10 | 1 | 2 | ol | TRUE
400330 | ЭГРЭС-1-500 - ТАВРИЧЕСКАЯ |  | 25 | 1817 | 1 | 11.8 | 108.2 | 4.5837 | 0 | 10 | 1 | 1 | ol | TRUE
400331 | Коунрад-220 - Актогай-220 |  | 481 | 483 | 1 | 36.6 | 154.8 | 3.2541 | 0 | 10 | 1 | 1 | ol | TRUE
400332 | Коунрад-220 - Актогай-220 |  | 481 | 483 | 1 | 36.6 | 154.8 | 3.2541 | 0 | 10 | 1 | 2 | ol | FALSE
400333 | Балхашская-220 - Mоинты |  | 473 | 475 | 1 | 16.46 | 70.14 | 1.4219 | 0 | 10 | 1 | 1 | ol | TRUE
400334 | ЭГРЭС-1-500 - НУРА-500 |  | 25 | 325 | 1 | 8.3 | 78.3 | 3.3423 | 0 | 10 | 1 | 1 | ol | TRUE
400335 | ШУ - ФРУНЗЕ |  | 9932 | 2919 | 1 | 2.82 | 28.85 | 1.1523 | 0 | 10 | 1 | 1 | ol | TRUE
400336 | ШУ - АЛМАТЫ |  | 9932 | 902 | 1 | 7.1 | 72.41 | 2.8998 | 0 | 10 | 1 | 1 | ol | TRUE
400337 | ШУ - ЮКГРЭС |  | 9932 | 900 | 1 | 5.2 | 63.6 | 2.5083 | 0 | 10 | 1 | 1 | ol | TRUE
400338 | Ру-6 - Шиели |  | 869 | 863 | 1 | 4.99 | 19.49 | 0.41062 | 0 | 10 | 1 | 1 | ol | TRUE
400339 | Жанакорган - Ру-6 |  | 865 | 869 | 1 | 7.21 | 28.31 | 0.59142 | 0 | 10 | 1 | 1 | ol | TRUE
400340 | ИРТЫШСКАЯ - ТАВРИЧЕСКАЯ |  | 1850 | 1817 | 1 | 3.42 | 35.28 | 1.3942 | 0 | 10 | 1 | 1 | ol | TRUE
400341 | Иртышская - Урожайная |  | 1851 | 1673 | 1 | 10.7 | 46.8 | 3.7529 | 0 | 10 | 1 | 1 | ol | FALSE
400342 | ТУЛЕБЕРДЫЕВА - ТОКТОГУЛЬСКАЯ ГЭС |  | 2915 | 2921 | 1 | 2.7 | 24.2 | 0.95493 | 0 | 10 | 1 | 1 | ol | FALSE
400343 | Главная - Карабалты |  | 2916 | 2917 | 1 | 7.9 | 33.2 | 0.78623 | 0 | 10 | 1 | 1 | ol | FALSE
400344 | Карабалты - Бишкек |  | 2917 | 2918 | 1 | 6.4 | 27 | 0.28648 | 0 | 10 | 1 | 1 | ol | FALSE
400345 | Карабалты - Бишкек |  | 2917 | 2918 | 1 | 6.4 | 27 | 0.28648 | 0 | 10 | 1 | 2 | ol | FALSE
400346 | ФРУНЗЕ - ТУЛЕБЕРДЫЕВА |  | 2919 | 2915 | 1 | 4.4 | 40 | 1.6297 | 0 | 10 | 1 | 1 | ol | FALSE
400347 | ЛОЧИН - УЗБЕКИСТОН |  | 2920 | 2922 | 1 | 4.85 | 44.22 | 1.8016 | 0 | 10 | 1 | 1 | ol | FALSE
400348 | УЗБЕКИСТОН - СЫРДАРЬИНСКАЯ ТЭС |  | 2922 | 2923 | 1 | 6.2 | 88 | 4.4245 | 0 | 10 | 1 | 1 | ol | FALSE
400349 | УЗБЕКИСТОН - НОВО-АНГРЕНСКАЯ ТЭС |  | 2922 | 2945 | 1 | 4.35 | 50.54 | 1.8939 | 0 | 10 | 1 | 1 | ol | FALSE
400350 | ТАШ.ГРЭС - ТАШКЕНТ |  | 2924 | 2940 | 1 | 0.45 | 5.81 | 0.2069 | 0 | 10 | 1 | 1 | ol | FALSE
400351 | Ташкент - Ташкентская грэс |  | 2925 | 2926 | 1 | 0.1 | 3 | 0.1 | 0 | 10 | 1 | 1 | ol | FALSE
400352 | ТАШКЕНТ - СЫРДАРЬИНСКАЯ ТЭС |  | 2940 | 2923 | 1 | 4.03 | 49.2 | 1.8526 | 0 | 10 | 1 | 1 | ol | FALSE
400353 | ТАШКЕНТ - НОВО-АНГРЕНСКАЯ ТЭС |  | 2940 | 2945 | 1 | 1.62 | 20 | 0.74803 | 0 | 10 | 1 | 1 | ol | FALSE
400354 | ЮЖНАЯ - РЕФТИНСКАЯ ГРЭС |  | 4701 | 4702 | 1 | 2.23 | 25.5 | 1.0504 | 0 | 10 | 1 | 1 | ol | TRUE
400355 | ЮЖНАЯ - КУРЧАТОВСКАЯ |  | 4701 | 50002 | 1 | 2.64 | 39.1 | 1.5966 | 0 | 10 | 1 | 1 | ol | TRUE
400356 | РЕФТИНСКАЯ ГРЭС - ИСЕТЬ |  | 4702 | 50001 | 1 | 3.5 | 35.55 | 1.4311 | 0 | 10 | 1 | 1 | ol | TRUE
400357 | РЕФТИНСКАЯ ГРЭС - ТЮМЕНЬ |  | 4702 | 4730 | 1 | 8.32 | 73.14 | 3.0399 | 0 | 10 | 1 | 1 | ol | TRUE
400358 | РЕФТИНСКАЯ ГРЭС - ТЮМЕНЬ |  | 4702 | 4730 | 1 | 8.32 | 73.14 | 3.0399 | 0 | 10 | 1 | 2 | ol | TRUE
400359 | КОЗЫРЕВО - КУРГАН |  | 4703 | 4727 | 1 | 9.02 | 84.65 | 3.3932 | 0 | 10 | 1 | 1 | ol | TRUE
400360 | ИСЕТЬ - КУРЧАТОВСКАЯ |  | 50001 | 50002 | 1 | 29.82 | 29.14 | 1.1836 | 0 | 10 | 1 | 1 | ol | TRUE
400361 | Усть-Камногорская-220 - ТМК |  | 241 | 242 | 1 | 3.27 | 21.8 | 0.49656 | 0 | 10 | 1 | 1 | ol | TRUE
400362 | Усть-Камногорская-220 - ТМК |  | 241 | 242 | 1 | 3.27 | 21.8 | 0.49656 | 0 | 10 | 1 | 2 | ol | TRUE
400363 | ПС-7 - Усть-Камногорская-220 |  | 215 | 241 | 1 | 4.3 | 6.8 | 0.39311 | 0 | 10 | 1 | 1 | ol | TRUE
400364 | ПС-7 - Усть-Камногорская-220 |  | 215 | 241 | 1 | 4.3 | 6.8 | 0.39311 | 0 | 10 | 1 | 2 | ol | TRUE
400365 | БАРНАУЛ-500 - Новокузнецкая |  | 1630 | 1638 | 1 | 7.8 | 77 | 3.0876 | 0 | 10 | 1 | 1 | ol | FALSE
400366 | АЛТАЙ - Итатская |  | 1660 | 1636 | 1 | 5 | 120 | 6.0479 | 0 | 10 | 1 | 1 | ol | FALSE
400367 | ЗАРЯ - Юрга |  | 1631 | 1632 | 1 | 2.56 | 31.7 | 1.512 | 0 | 10 | 1 | 1 | ol | FALSE
400368 | Шымкент-220 - Жылга |  | 831 | 839 | 1 | 19.96 | 79.35 | 1.6546 | 0 | 10 | 1 | 1 | ol | TRUE
400369 | Кызылсай - Жамбыл |  | 845 | 801 | 1 | 17.66 | 71.61 | 1.4203 | 0 | 10 | 1 | 1 | ol | TRUE
400370 | Шу - Чиганак |  | 932 | 925 | 1 | 22.96 | 102.12 | 2.005 | 0 | 10 | 1 | 1 | ol | TRUE
400371 | отпайка - гпп-2 |  | 861 | 5957 | 1 | 27.9 | 108.86 | 2.2173 | 0 | 10 | 1 | 1 | ol | TRUE
400372 | юкгрэс - Mоинты |  | 901 | 475 | 1 | 26.49 | 115.13 | 2.3405 | 0 | 10 | 1 | 1 | ol | TRUE
400373 | нс-19 - эгрэс-1 |  | 309 | 39 | 1 | 28.98 | 114.36 | 2.3622 | 0 | 10 | 1 | 1 | ol | TRUE
400374 | грэс-2 - Айса |  | 355 | 452 | 1 | 14.4 | 56.87 | 1.1714 | 0 | 10 | 1 | 1 | ol | TRUE
400375 | Апановка - Есиль |  | 573 | 170 | 1 | 21.65 | 83.62 | 2.9603 | 0 | 10 | 1 | 1 | ol | TRUE
400376 | Есиль - Перекатная (т) |  | 170 | 172 | 1 | 12.4 | 55.4 | 1.0883 | 0 | 10 | 1 | 1 | ol | TRUE
400377 | Атбасар - Жалтыр (т) |  | 134 | 132 | 1 | 11.6 | 51.5 | 1.0103 | 0 | 10 | 1 | 2 | ol | TRUE
400378 | цгпп - Жалтыр (т) |  | 130 | 132 | 1 | 11.4 | 51.1 | 1.002 | 0 | 10 | 1 | 2 | ol | TRUE
400379 | цгпп - Еркеншилик (т) |  | 130 | 167 | 1 | 9.5 | 42.7 | 0.83779 | 0 | 10 | 1 | 1 | ol | TRUE
400380 | Танкерис (т) - Макинск |  | 179 | 150 | 1 | 16.8 | 75.2 | 1.4776 | 0 | 10 | 1 | 1 | ol | TRUE
400381 | жгрэс-220 - Мерке |  | 805 | 809 | 1 | 16.63 | 62.03 | 1.3923 | 0 | 10 | 1 | 1 | ol | TRUE
400382 | Главная - Кемин |  | 2916 | 2952 | 1 | 11.64 | 50.13 | 1.0246 | 0 | 10 | 1 | 1 | ol | TRUE
400383 | ФРУНЗЕ - ТОКТОГУЛЬСКАЯ ГЭС |  | 2919 | 2921 | 1 | 7.1 | 64.2 | 2.5847 | 0 | 10 | 1 | 1 | ol | TRUE
400384 | Главная - Бишкек |  | 2916 | 2918 | 1 | 11.1 | 46.7 | 1.3592 | 0 | 10 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service | pt_percent | oltc
500001 | УЛЬКЕ-500 - Ульке-220 |  | 9001 | 3020 | 501 | 500 | 220 | 11 | 0.189 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500002 | Актогай-220 - Актогай-110 |  | 483 | 484 | 250 | 220 | 110 | 11 | 0.189 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500003 | ВОСХОД - Восход |  | 1853 | 1854 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500004 | ЦГПП - цгпп |  | 129 | 130 | 501 | 500 | 220 | 11 | 0.147 | 172 | 0.246 | 0 | [7 empty] | FALSE | 2 | 1 | TRUE |  | FALSE
500005 | СОКОЛ-500 - Сокол-220 |  | 576 | 575 | 501 | 500 | 220 | 11 | 0.147 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500006 | СОКОЛ-500 - Сокол-220 |  | 576 | 575 | 501 | 500 | 220 | 11 | 0.147 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500007 | КОСТАНАЙСКАЯ - Кустанайская |  | 590 | 592 | 501 | 500 | 220 | 11 | 0.147 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500008 | ЖИТИКАРА-500 - Житикара-110 |  | 577 | 578 | 250 | 500 | 110 | 10 | 0.42 | 220 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500009 | ЭГРЭС-1-500 - эгрэс-1 |  | 25 | 39 | 801 | 500 | 220 | 8.6 | 0.0251 | 297.45 | 0.15 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500010 | ЭГРЭС-1-500 - эгрэс-1-бл3-8 |  | 25 | 51 | 630 | 500 | 20 | 14.2 | 0.203 | 270.97 | 0.058 | 0 | [7 empty] | FALSE | 6 | 1 | TRUE |  | FALSE
500011 | ЭГРЭС-2-500 - эгрэс-2-20 |  | 28 | 60 | 630 | 500 | 20 | 14.7 | 0.203 | 380 | 0.21 | 0 | [7 empty] | FALSE | 2 | 1 | TRUE |  | FALSE
500012 | ЕЭК-500 - еэк-20-бл5-8 |  | 31 | 30 | 400 | 500 | 20 | 12.6 | 0.20075 | 370 | 0.54 | 0 | [7 empty] | FALSE | 3 | 1 | TRUE |  | FALSE
500013 | ЕЭК-500 - еэк-220 |  | 31 | 33 | 801 | 500 | 220 | 11.9 | 0.17 | 273.3 | 0.291 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500014 | еэк-220 - еэк-20-бл2-4 |  | 33 | 32 | 630 | 220 | 20 | 10.7 | 0.219 | 274 | 0.5 | 0 | [7 empty] | FALSE | 3 | 1 | TRUE |  | FALSE
500015 | эгрэс-1 - эгрэс-1-бл2 |  | 39 | 50 | 630 | 220 | 20 | 12.5 | 0.206 | 380 | 0.35 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500016 | УСТЬ-КАМЕНОГРСКАЯ-500 - Усть-Камногорская-220 |  | 240 | 241 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500017 | УСТЬ-КАМЕНОГРСКАЯ-500 - Усть-Камногорская-220 |  | 240 | 241 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500018 | шгэс-220 - шгэс-14 |  | 220 | 221 | 250 | 220 | 14 | 11 | 0.24 | 207 | 0.5 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500019 | жтэц-220 - жтэц |  | 463 | 462 | 125 | 220 | 110 | 11.8 | 0.25 | 219.37 | 0.37 | 0 | [7 empty] | FALSE | 2 | 1 | FALSE |  | FALSE
500020 | Никольская - Никольская |  | 464 | 461 | 125 | 220 | 110 | 11 | 0.252 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500021 | Кумколь - Кумколь |  | 467 | 455 | 125 | 220 | 110 | 11 | 0.252 | 65 | 0.4 | 0 | [7 empty] | FALSE | 2 | 1 | TRUE |  | FALSE
500022 | АГАДЫРЬ-500 - Aгадырь-220 |  | 469 | 468 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500023 | Балхашская-220 - Балхашская-110 |  | 473 | 472 | 125 | 220 | 110 | 11 | 0.252 | 65 | 0.4 | 0 | [7 empty] | FALSE | 2 | 1 | TRUE |  | FALSE
500024 | ЖЕЗКАЗГАН-500 - Жезказган-220 |  | 480 | 466 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500025 | ЮКГРЭС - юкгрэс |  | 900 | 901 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500026 | АЛМАТЫ - Алматы |  | 902 | 903 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.246 | 0 | [7 empty] | FALSE | 2 | 1 | TRUE |  | FALSE
500027 | Капчагайская гэс-220 - Капчагайская гэс-14 |  | 909 | 910 | 125 | 220 | 15 | 11 | 0.304 | 135 | 0.5 | 0 | [7 empty] | FALSE | 2 | 1 | FALSE |  | FALSE
500028 | Мойнакская гэс-220 - Мойнакская гэс-15-1 |  | 935 | 937 | 200 | 220 | 15 | 10.5 | 0.275 | 140 | 0.5 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500029 | пс-7 - пс-7 |  | 912 | 913 | 250 | 220 | 110 | 11 | 0.208 | 65 | 0.4 | 0 | [7 empty] | FALSE | 2 | 1 | TRUE |  | FALSE
500030 | ЖАМБЫЛ - Жамбыл |  | 800 | 801 | 501 | 500 | 220 | 10.5 | 0.060413 | 206.49 | 0.35 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500031 | жгрэс-220 - жгрэс-16 |  | 805 | 806 | 250 | 220 | 15 | 11.8 | 0.25 | 219.37 | 0.37 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500032 | жгрэс-220 - жгрэс-110 |  | 805 | 807 | 240 | 220 | 110 | 12.6 | 0.155 | 368 | 1.3 | 0 | [7 empty] | FALSE | 2 | 1 | FALSE |  | FALSE
500033 | ШЫМКЕНТ-500 - Шымкент-220 |  | 830 | 831 | 501 | 500 | 220 | 11.8 | 0.072056 | 168.9 | 0.3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500034 | ШЫМКЕНТ-500 - Шымкент-220 |  | 830 | 831 | 501 | 500 | 220 | 11.8 | 0.072056 | 168.9 | 0.3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500035 | Коунрад-220 - Коунрад-110 |  | 481 | 482 | 63 | 220 | 110 | 11 | 0.317 | 37 | 0.45 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500036 | цгпп - цгпп |  | 130 | 124 | 250 | 220 | 110 | 11 | 0.208 | 145 | 0.5 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500037 | цгпп - цгпп |  | 130 | 124 | 250 | 220 | 110 | 11 | 0.208 | 145 | 0.5 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500038 | КОКЧЕТАВСКАЯ - Кокшетауская-1150 |  | 175 | 176 | 501 | 500 | 220 | 11 | 0.147 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500039 | ЕСИЛЬ - Есиль |  | 180 | 170 | 501 | 500 | 220 | 11 | 0.147 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500040 | ЦГПП - цгпп |  | 129 | 130 | 501 | 500 | 220 | 11 | 0.147 | 172 | 0.246 | 0 | [7 empty] | FALSE | 2 | 1 | TRUE |  | FALSE
500041 | АВРОРА - Аврора |  | 147 | 148 | 501 | 500 | 220 | 11 | 0.147 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500042 | АВРОРА - Аврора |  | 147 | 148 | 501 | 500 | 220 | 11 | 0.147 | 172 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500043 | Сибирь - Сибирь |  | 161 | 160 | 63 | 220 | 110 | 11 | 0.317 | 37 | 0.45 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500044 | СЕМЕЙ-500 - Семей-220 |  | 980 | 981 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500045 | Актогай-220 - Актогай-110 |  | 483 | 484 | 63 | 220 | 110 | 11 | 0.317 | 37 | 0.45 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500046 | АЛМА - Алма |  | 938 | 939 | 501 | 500 | 220 | 11 | 0.188 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500047 | АЛМА - Алма |  | 938 | 939 | 501 | 500 | 220 | 11 | 0.188 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500048 | ТАЛДЫКОРГАН-500 - Талдыкорган-220 |  | 987 | 988 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500049 | АЛМАТЫ - Алматы |  | 902 | 903 | 501 | 500 | 220 | 11 | 0.188 | 270 | 0.246 | 0 | [7 empty] | FALSE | 2 | 1 | TRUE |  | FALSE
500050 | КЕМИН - Кемин |  | 2951 | 2952 | 501 | 500 | 220 | 11.5 | 0.209 | 230 | 0.3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500051 | КЕМИН - Кемин |  | 2951 | 2952 | 501 | 500 | 220 | 11.5 | 0.209 | 230 | 0.3 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500052 | Акжар - арбз |  | 3004 | 4004 | 200 | 220 | 110 | 11 | 0.215 | 48 | 0.45 | 0 | [7 empty] | FALSE | 2 | 1 | FALSE |  | FALSE
500053 | вэс ерейментау - wtu 2.0 |  | 155 | 191 | 63 | 220 | 35 | 11 | 0.2 | 40 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500054 | НУРА-500 - Нура-220 |  | 325 | 310 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500055 | птэц-2-220 - птэц-2-110 |  | 144 | 142 | 125 | 220 | 110 | 11 | 0.252 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500056 | птэц-2-220 - птэц-2-110 |  | 144 | 142 | 125 | 220 | 110 | 11 | 0.252 | 65 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500057 | ТРОИЦКАЯ ГРЭС - Троицкая грэс |  | 4799 | 4798 | 630 | 500 | 220 | 11.62 | 0.224 | 0 | 0 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500058 | РУБЦОВСКАЯ - Рубцовская |  | 1621 | 1622 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500059 | БАРНАУЛ-500 - Барнаул-220 |  | 1630 | 1640 | 501 | 500 | 220 | 11 | 0.188 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500060 | БАРНАУЛ-500 - Барнаул-220 |  | 1630 | 1640 | 501 | 500 | 220 | 11 | 0.188 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500061 | Мойнакская гэс-220 - Мойнакская гэс-15-2 |  | 935 | 941 | 200 | 220 | 15 | 10.5 | 0.275 | 140 | 0.5 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500062 | Коунрад-220 - Коунрад-110 |  | 481 | 482 | 63 | 220 | 110 | 11 | 0.317 | 37 | 0.45 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500063 | Экибастуз-220 - Экибастузская тэц |  | 38 | 44 | 1250 | 220 | 6 | 0.59 | 0 | 0 | 0 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500064 | ТАВРИЧЕСКАЯ - Таврическая |  | 1817 | 1816 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500065 | ТАВРИЧЕСКАЯ - Таврическая |  | 1817 | 1816 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500066 | ШУ - Шу |  | 9932 | 932 | 501 | 500 | 220 | 9.5 | 0.031 | 105 | 0.4 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500067 | ИРТЫШСКАЯ - Иртышская |  | 1850 | 1851 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500068 | ФРУНЗЕ - Бишкек |  | 2919 | 2918 | 501 | 500 | 220 | 11 | 0.188 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500069 | ФРУНЗЕ - Бишкек |  | 2919 | 2918 | 501 | 500 | 220 | 11 | 0.188 | 270 | 0.246 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500070 | ТАШ.ГРЭС - Ташкент |  | 2924 | 2925 | 501 | 500 | 220 | 11 | 0.189 | 270 | 0.55 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE
500071 | ИРИКЛИНСКАЯ ГРЭС - Ириклинская грэс |  | 4790 | 4791 | 800 | 500 | 220 | 11.5 | 0.176 | 375 | 0.25 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500072 | бтэц-110 - бтэц-10 |  | 471 | 470 | 80 | 110 | 10 | 10.5 | 0.387 | 70 | 0.6 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500073 | ИРИКЛИНСКАЯ ГРЭС - Ириклинская грэс |  | 4790 | 4791 | 800 | 500 | 220 | 11.5 | 0.176 | 375 | 0.25 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE
500074 | БАРАБИНСКАЯ - Барабинская-220 |  | 9917 | 1671 | 501 | 500 | 220 | 11.2 | 0.212 | 0 | 0 | 0 | [7 empty] | FALSE | 1 | 1 | FALSE |  | FALSE

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
25
26
27
28
29
30
31
32
33
36
37
38
39
44
50
51
52
53
54
55
56
58
59
60
61
62
101
102
103
104
108
123
124
125
126
129
130
132
134
135
136
142
143
144
147
148
150
151
153
155
156
157
159
160
161
162
163
164
165
166
167
169
170
172
173
175
176
178
179
180
186
191
214
215
218
220
221
222
240
241
242
251
306
307
308
309
310
314
315
318
325
355
383
384
450
451
452
453
454
455
457
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
480
481
482
483
484
571
572
573
574
575
576
577
578
582
585
590
592
593
594
595
596
800
801
802
803
804
805
806
807
809
810
813
814
815
816
817
830
831
834
835
836
837
838
839
840
841
842
843
844
845
846
860
861
862
863
865
866
867
869
900
901
902
903
904
907
908
909
910
911
912
913
918
924
925
928
929
930
931
932
935
937
938
939
940
941
942
950
951
953
980
981
986
987
988
1621
1622
1630
1631
1632
1636
1638
1640
1660
1671
1673
1816
1817
1850
1851
1852
1853
1854
2915
2916
2917
2918
2919
2920
2921
2922
2923
2924
2925
2926
2932
2940
2945
2950
2951
2952
3004
3005
3006
3019
3020
3102
3103
3104
4004
4701
4702
4703
4705
4709
4712
4714
4715
4727
4728
4730
4781
4782
4785
4790
4791
4798
4799
5957
5958
9001
9917
9932
47161
50001
50002
50014
50032

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
400001
400002
400003
400004
400005
400006
400007
400008
400009
400010
400011
400012
400013
400014
400015
400016
400017
400018
400019
400020
400021
400022
400023
400024
400025
400026
400027
400028
400029
400030
400031
400032
400033
400034
400035
400036
400037
400038
400039
400040
400041
400042
400043
400044
400045
400046
400047
400048
400049
400050
400051
400052
400053
400054
400055
400056
400057
400058
400059
400060
400061
400062
400063
400064
400065
400066
400067
400068
400069
400070
400071
400072
400073
400074
400075
400076
400077
400078
400079
400080
400081
400082
400083
400084
400085
400086
400087
400088
400089
400090
400091
400092
400093
400094
400095
400096
400097
400098
400099
400100
400101
400102
400103
400104
400105
400106
400107
400108
400109
400110
400111
400112
400113
400114
400115
400116
400117
400118
400119
400120
400121
400122
400123
400124
400125
400126
400127
400128
400129
400130
400131
400132
400133
400134
400135
400136
400137
400138
400139
400140
400141
400142
400143
400144
400145
400146
400147
400148
400149
400150
400151
400152
400153
400154
400155
400156
400157
400158
400159
400160
400161
400162
400163
400164
400165
400166
400167
400168
400169
400170
400171
400172
400173
400174
400175
400176
400177
400178
400179
400180
400181
400182
400183
400184
400185
400186
400187
400188
400189
400190
400191
400192
400193
400194
400195
400196
400197
400198
400199
400200
400201
400202
400203
400204
400205
400206
400207
400208
400209
400210
400211
400212
400213
400214
400215
400216
400217
400218
400219
400220
400221
400222
400223
400224
400225
400226
400227
400228
400229
400230
400231
400232
400233
400234
400235
400236
400237
400238
400239
400240
400241
400242
400243
400244
400245
400246
400247
400248
400249
400250
400251
400252
400253
400254
400255
400256
400257
400258
400259
400260
400261
400262
400263
400264
400265
400266
400267
400268
400269
400270
400271
400272
400273
400274
400275
400276
400277
400278
400279
400280
400281
400282
400283
400284
400285
400286
400287
400288
400289
400290
400291
400292
400293
400294
400295
400296
400297
400298
400299
400300
400301
400302
400303
400304
400305
400306
400307
400308
400309
400310
400311
400312
400313
400314
400315
400316
400317
400318
400319
400320
400321
400322
400323
400324
400325
400326
400327
400328
400329
400330
400331
400332
400333
400334
400335
400336
400337
400338
400339
400340
400341
400342
400343
400344
400345
400346
400347
400348
400349
400350
400351
400352
400353
400354
400355
400356
400357
400358
400359
400360
400361
400362
400363
400364
400365
400366
400367
400368
400369
400370
400371
400372
400373
400374
400375
400376
400377
400378
400379
400380
400381
400382
400383
400384

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
500001
500002
500003
500004
500005
500006
500007
500008
500009
500010
500011
500012
500013
500014
500015
500016
500017
500018
500019
500020
500021
500022
500023
500024
500025
500026
500027
500028
500029
500030
500031
500032
500033
500034
500035
500036
500037
500038
500039
500040
500041
500042
500043
500044
500045
500046
500047
500048
500049
500050
500051
500052
500053
500054
500055
500056
500057
500058
500059
500060
500061
500062
500063
500064
500065
500066
500067
500068
500069
500070
500071
500072
500073
500074

## res_ext_grid
| p_mw | q_mvar
47090

## res_load
| p_mw | q_mvar
200001
200002
200003
200004
200005
200006
200007
200008
200009
200010
200011
200012
200013
200014
200015
200016
200017
200018
200019
200020
200021
200022
200023
200024
200025
200026
200027
200028
200029
200030
200031
200032
200033
200034
200035
200036
200037
200038
200039
200040
200041
200042
200043
200044
200045
200046
200047
200048
200049
200050
200051
200052
200053
200054
200055
200056
200057
200058
200059
200060
200061
200062
200063
200064
200065
200066
200067
200068
200069
200070
200071
200072
200073
200074
200075
200076
200077
200078
200079
200080
200081
200082
200083
200084
200085
200086
200087
200088
200089
200090
200091
200092
200093
200094
200095
200096
200097
200098
200099
200100
200101
200102
200103
200104
200105
200106
200107
200108
200109
200110
200111
200112
200113
200114
200115
200116
200117
200118
200119
200120
200121
200122
200123
200124
200125
200126
200127
200128
200129
200130
200131
200132
200133
200134
200135
200136
200137
200138
200139
200140
200141
200142
200143
200144
200145
200146
200147
200148
200149
200150
200151
200152
200153
200154
200155
200156
200157
200158
200159
200160
200161
200162
200163
200164
200165
200166
200167
200168
200169
200170
200171
200172
200173
200174
200175
200176
200177
200178
200179
200180
200181
200182
200183
200184
200185
200186
200187
200188
200189
200190
200191
200192
200193
200194
200195
200196
200197
200198
200199
200200
200201
200202
200203
200204
200205
200206
200207
200208
200209
200230

## res_shunt
| p_mw | q_mvar | vm_pu
600001
600002
600003
600004
600005
600006
600007
600008
600009
600010
600011
600012
600013
600014
600015
600016
600017
600018
600019
600020
600021
600022
600023
600024
600025
600026
600027
600028
600029
600030
600031
600032
600033
600034
600035
600036
600037
600038
600039
600040
600041
600042
600043
600044
600045
600046
600047
600048
600049
600050
600051
600052
600053
600054
600055

## res_gen
| p_mw | q_mvar | va_degree | vm_pu
300001
300002
300003
300004
300005
300006
300007
300008
300009
300010
300013
300014
300015
300016
300017
300018
300019
300020
300021
300022
300023
300024
300025
300026
300027
300028
300029
300030
300031
300032
300033
300034
300035
300036
300037
300038
300039
300040
300041
300042
300043
300044
300045
300046
300047
300048
300049
300050
300051
300052
300053
300054
300055
300056
300057
300058
300059
300060
300061
300062
300063
300064
300065
300066
300067
300068
300069
300070
300071
300072
300073
300074
300075
300076
300077
300078
300079
300080
300081
300082
300083
300084
300085
300086
300087
300088
300089
300090
300091
300092
300093
300094
300095
300096
300097
300098
300099
300100
300101
300102
300103
300104
300105
300106
300107
300108
300109
300110
300111
300112
300113
300114
300115
300116
300117
300118
300119
300120
300121
300122
300123
300124
300125
300126
300127
300128
300129
300130
300131
300132
300133
300134
300135
300136
300137
300138
300139
300140
300141
300142
300143
300144
300145
300146
300147
300148
300149
300150
300151
300152
300153
300154
300155
300156
300157
300158
300159
300160
300161
300162
300163
300164
300165
300166
300167
300168
300169
300170
300171
300172
300173
300174
300175
300176
300177
300178
300179
300180
300181
300182
300183
300184
300185
300186
300187
300188
300189
300190
300191
300192
300193
300194
300195
300196
300197
300198
300199
300200
300201
300202
300203
300204
300205
300206
300207
300208
300209

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | gen | name | object
16 | gen | bus | uint32
17 | gen | p_mw | float64
18 | gen | vm_pu | float64
19 | gen | sn_mva | float64
20 | gen | min_q_mvar | float64
21 | gen | max_q_mvar | float64
22 | gen | scaling | float64
23 | gen | slack | bool
24 | gen | in_service | bool
25 | gen | slack_weight | float64
26 | gen | type | object
27 | gen | power_station_trafo | float64
28 | shunt | bus | uint32
29 | shunt | name | object
30 | shunt | q_mvar | float64
31 | shunt | p_mw | float64
32 | shunt | vn_kv | float64
33 | shunt | step | uint32
34 | shunt | max_step | uint32
35 | shunt | in_service | bool
36 | ext_grid | name | object
37 | ext_grid | bus | uint32
38 | ext_grid | vm_pu | float64
39 | ext_grid | va_degree | float64
40 | ext_grid | slack_weight | float64
41 | ext_grid | in_service | bool
42 | line | name | object
43 | line | std_type | object
44 | line | from_bus | uint32
45 | line | to_bus | uint32
46 | line | length_km | float64
47 | line | r_ohm_per_km | float64
48 | line | x_ohm_per_km | float64
49 | line | c_nf_per_km | float64
50 | line | g_us_per_km | float64
51 | line | max_i_ka | float64
52 | line | df | float64
53 | line | parallel | uint32
54 | line | type | object
55 | line | in_service | bool
56 | trafo | name | object
57 | trafo | std_type | object
58 | trafo | hv_bus | uint32
59 | trafo | lv_bus | uint32
60 | trafo | sn_mva | float64
61 | trafo | vn_hv_kv | float64
62 | trafo | vn_lv_kv | float64
63 | trafo | vk_percent | float64
64 | trafo | vkr_percent | float64
65 | trafo | pfe_kw | float64
66 | trafo | i0_percent | float64
67 | trafo | shift_degree | float64
68 | trafo | tap_side | object
69 | trafo | tap_neutral | float64
70 | trafo | tap_min | float64
71 | trafo | tap_max | float64
72 | trafo | tap_step_percent | float64
73 | trafo | tap_step_degree | float64
74 | trafo | tap_pos | float64
75 | trafo | tap_phase_shifter | bool
76 | trafo | parallel | uint32
77 | trafo | df | float64
78 | trafo | in_service | bool
79 | trafo | pt_percent | float64
80 | trafo | oltc | object
81 | res_bus | vm_pu | float64
82 | res_bus | va_degree | float64
83 | res_bus | p_mw | float64
84 | res_bus | q_mvar | float64
85 | res_line | p_from_mw | float64
86 | res_line | q_from_mvar | float64
87 | res_line | p_to_mw | float64
88 | res_line | q_to_mvar | float64
89 | res_line | pl_mw | float64
90 | res_line | ql_mvar | float64
91 | res_line | i_from_ka | float64
92 | res_line | i_to_ka | float64
93 | res_line | i_ka | float64
94 | res_line | vm_from_pu | float64
95 | res_line | va_from_degree | float64
96 | res_line | vm_to_pu | float64
97 | res_line | va_to_degree | float64
98 | res_line | loading_percent | float64
99 | res_trafo | p_hv_mw | float64
100 | res_trafo | q_hv_mvar | float64
101 | res_trafo | p_lv_mw | float64
102 | res_trafo | q_lv_mvar | float64
103 | res_trafo | pl_mw | float64
104 | res_trafo | ql_mvar | float64
105 | res_trafo | i_hv_ka | float64
106 | res_trafo | i_lv_ka | float64
107 | res_trafo | vm_hv_pu | float64
108 | res_trafo | va_hv_degree | float64
109 | res_trafo | vm_lv_pu | float64
110 | res_trafo | va_lv_degree | float64
111 | res_trafo | loading_percent | float64
112 | res_ext_grid | p_mw | float64
113 | res_ext_grid | q_mvar | float64
114 | res_load | p_mw | float64
115 | res_load | q_mvar | float64
116 | res_shunt | p_mw | float64
117 | res_shunt | q_mvar | float64
118 | res_shunt | vm_pu | float64
119 | res_gen | p_mw | float64
120 | res_gen | q_mvar | float64
121 | res_gen | va_degree | float64
122 | res_gen | vm_pu | float64